## Slide 1: Duct Design Fundamentals – Equal Friction Method
Stephen Idem
ASHRAE TC 5.2 YEA Seminar

## Slide 2: Energy Equation for Air Flow in a Duct
Assume the following:
Adiabatic flow
Negligible elevation changes
Constant density
No fan is present

## Slide 3: Static and Velocity Pressure Differences for Air Flow in a Duct

## Slide 4: Velocity Pressure
Velocity pressure is a measure of the kinetic energy of the air flowing in a duct system:

## Slide 5: Energy Equation Expressed in Terms of Total Pressure Change
The total pressure at any location is the sum of its static and velocity pressures:

## Slide 6: Head Losses
Minor Head Loss:
The total head loss is the sum of the major and minor head losses:
Major Head Loss:

## Slide 7: Fitting (Minor) Losses
The fitting loss coefficient represents the ratio of total pressure loss to velocity pressure at a reference cross section.
All dynamic losses are assumed to be concentrated at a section (i.e. local) and to exclude friction.

## Slide 8: Duct Mounted Fitting Loss Coefficient – ASHRAE Standard 120

## Slide 9: Duct Mounted Fitting Loss Coefficient – ASHRAE Standard 120

## Slide 10: Divided Flow Fitting Loss Coefficient – ASHRAE Standard 120

## Slide 11: Divided Flow Fitting Loss Coefficient – ASHRAE Standard 120
Per ASHRAE Standard 120 the main and branch loss coefficients, respectively, for a diverging fittings are defined as:

## Slide 12: ASHRAE Duct Fitting Database (DFDB)
The DFDB uses a unique nomenclature to identify each fitting/duct-mounted component. Entries and converging junctions are only for exhaust/return portion of systems.
Exits and diverging junctions are only for supply systems.
Equal-area elbows, obstructions, and duct-mounted equipment are common to both supply and exhaust/return systems.
Transitions and unequal-area elbows are both supply or exhaust/return fittings, each referenced to the appropriate cross-section and direction of airflow.
Fitting Function | Geometry | Category | Sequential Number
S: Supply | D: Round | 1: Entries | 1, 2, 3 … n
E: Exhaust/return | R: Rectangular | 2: Exits | 
C: Common | F: Flat oval | 3: Elbows | 
 |  | 4: Transitions | 
 |  | 5: Junctions | 
 |  | 6: Obstructions | 
 |  | 7: Fan and system interactions | 
 |  | 8: Duct-mounted equipment | 
 |  | 9: Dampers | 
 |  | 10: Hoods | 
 |  | 11: Straight ducts | 

## Slide 13: Moody Diagram

## Slide 14: Darcy Friction Factor
Colebrook Equation:
Haaland Equation:

## Slide 15: Darcy-Weisbach Equation
The pressure loss for each section of a duct system can be determined using the Darcy-Weisbach equation:


## Slide 16: Equal Friction Duct Design Method
The principle of this method is to make the pressure loss per unit length of duct the same for the entire system.
A typical procedure for low velocity systems is to select the duct size in the main line adjacent to the fan such that:

## Slide 17: Equal Friction Duct Design Example

## Slide 18: Equal Friction Example - Duct Layout

## Slide 19: Table 3-1 Maximum Recommended Duct Airflow Velocities to Achieve Specified Acoustic Design Criteria (Schaffer 2005; Table 8, ASHRAE 2019)
Duct Location | RC or NC Rating in Adjacent Occupancy | Maximum Airflow Velocity, fpm | 
 |  | Rectangular Duct | Round Duct
In shaft or above drywall ceiling | 45 | 3500 | 5000
 | 35 | 2500 | 3500
 | 25 or less | 1700 | 2500
Above suspended acoustic ceiling | 45 | 2500 | 4500
 | 35 | 1750 | 3000
 | 25 or less | 1200 | 2000
Within occupied space | 45 | 2000 | 3900
 | 35 | 1450 | 2600
 | 25 or less | 950 | 1700

## Slide 20: Friction Chart

## Slide 21: Design Friction Rate
Based on the maximum recommended duct airflow velocity of 2,500 ft/min to achieve a desired acoustic criterion NC 25, DFDB fitting CD11-3 (or the friction chart) is used to calculate the diameter of section A as 16 in., with a design friction rate of 0.47 in. water per 100 ft.
The friction pressure loss in section A is:

## Slide 22: Loss Coefficients From the ASHRAE DFDB
SD5-7 | CD3-20 | SD5-9 | CD3-9 | CD3-5 | CD3-20
System effect for vaneaxial fan with mitered elbow; 16 in. diameter | Mitered elbow with turning vanes; 16 in. diameter | Diverging tee; 16 in. common, 14 in. branch, and 12 in. straight | 5-gore 90 elbow with r/D = 1.5; 14 in. diameter | Pleated 90 elbow with r/D = 1.5; 12 in. diameter | Mitered elbow with turning vanes; 12 in. diameter
C = 0.40 | C = 0.41 | Cb = 2.00 Cs = 0.13 | C = 0.17 | C = 0.26 | C = 0.45
The supply terminal is assumed to have the following loss coefficient: C = 1.25 |  |  |  |  | 

## Slide 23: Total Pressure Loss for Section A
The average velocity through section A is:
The total pressure loss for section A is:

## Slide 24: Sizing Section B Based on the Prescribed Friction Rate
Based on the design friction rate of 0.47 in. water per 100 ft, DFDB fitting CD11-4 (or the friction chart) is used to size the diameter of section B as 14 in.
The friction pressure loss in section B is:

## Slide 25: Total Pressure Loss From the Fan to the Diffuser in Section AB
The average velocity through section B is:
The total pressure loss for section B is:

## Slide 26: Sizing Section C Based on the Prescribed Friction Rate
Based on the design friction rate of 0.47 in. water per 100 ft, DFDB fitting CD11-4 (or the friction chart) is used to size the diameter of section C as 12 in.
The friction pressure loss in section C is:

## Slide 27: Total Pressure Loss From the Fan to the Diffuser in Section AC
The average velocity through section C is:
The total pressure loss for section C is:

## Slide 28: Total Pressure Loss
The total pressure loss from the fan to the diffuser in section AB is:
The total pressure loss from the fan to the diffuser in section AC is:

## Slide 29: Critical Path
The path with the greatest total pressure loss is the critical path.
In this case the critical path contains sections A and B.
The total pressure required at the fan outlet is 1.204 in. water.

## Slide 30: Excess Pressure
In the previous example 0.176 in. water additional pressure must be added to the path containing sections A and C in order to achieve the design flow rates.
Two options are generally available:
Add resistance using a balancing damper.
Design more resistance into the non-critical path using smaller duct sizes or less efficient fittings.

## Slide 31: Additional Considerations
Duct absolute roughness and fitting loss coefficients have a strong influence on the pressure loss of a section.
Even if the runs are nearly equal in length the system my still be out of balance.
It is not possible to select a ‘best’ friction rate because first cost and operating costs are not design parameters in the equal friction method.

## Slide 32: Equal Friction Duct Design Method Comments
If the layout is symmetrical with all runs from the fan to the diffuser about the same length this method will produce a nearly balanced system.
Most duct systems have a variety of duct runs ranging from short to long.
Typically short runs will have to be dampered to balance the flow.
Dampering can introduce considerable noise.