## Slide 1: TC Seminar ID# 23864 How Accurate is Your Air Flow Capture Hood Measurement? -- Residential Applications --
Steven Rogers, The Energy Conservatory
Clayton Hansen, The Energy Conservatory
Gary Nelson, The Energy Conservatory

## Slide 2: Learning Objectives
Understand the motivation for and characteristics of measuring and balancing residential HVAC systems
Understand the difference between and importance of accuracy and insertion loss
Understand how various styles of air flow hoods perform in residential applications in terms of both accuracy and insertion loss
Be able to draw some basic conclusions about how flow hood performance affects the ability to balance a residential HVAC system.

## Slide 3: Acknowledgements
Research was conducted by The Energy Conservatory, Inc.
Steven Rogers is employed by and the owner of The Energy Conservatory, Inc.

## Slide 4: Overview
Background and characteristics of measuring and balancing residential HVAC systems
Example: the need for measuring and balancing
Explain the test setup
Explain the hoods, supply registers, and orientations we tested
Show the results of the tests
Explain the conclusions from the test data and example

## Slide 5: Characteristics of Residential Air Flow Hood Applications
Smaller size and lower flow than commercial
Wide diversity of diffusers
Accessibility challenges
  Between toilet and wall
  Crown Molding
  Toe Kick

## Slide 6: Measuring and Balancing Supply Registers
Seldom measured or balanced in practice, why?
  Perception that it is not necessary
  Tools are too expensive
  Tools are designed for 24 x 24 inch (610 x 610 mm) commercial diffusers
  Some registers “impossible” to measure
Is there really a need to measure and balance?
  Let’s ask the “Jones” Family (name has been changed)

## Slide 7: “Jones” home near Minneapolis, MN
2 Story Colonial, 3100 ft2 (288 m2)
Basement Mostly Finished and Conditioned
Well Insulated Walls and Attic
Good Air tightness: 2.4 ACH50
Comfort Complaints
  Master Suite under conditioned
  West Bedrooms over conditioned
All their neighbors have similar comfort complaints

## Slide 8: “Jones” Home – As Found: Main Damper Closed
Living Room
Family Room
Dining Room
Kitchen
Mud Room
Foyer
Bedroom 1
Bedroom 2
MBR
Bath
WIC
M. Bath
Bedroom 3
Garage
144
4
4
6
5
9
6
9
Total Main Floor
187
3
114
115
0
0
0
4
4
Air Handler Total Flow
536 CFM (910 m3/hr)
Static Pressure in Supply Plenum
0.53 in W.C. (132 Pa)
Total Second Floor
240
Furnace Location in Basement

## Slide 9: “Jones” Home – As Designed/ Built
Living Room
Family Room
Dining Room
Kitchen
Mud Room
Foyer
71
55
19
13
10
22
6
23
Bedroom 1
Bedroom 2
MBR
Bath
WIC
M. Bath
Air Handler Total Flow
619 CFM (1052 m3/hr)
15% More Flow
Static Pressure in Supply Plenum
0.10 in W.C. (24 Pa)
Less than 1/5!
54
44
19
21
21
8
2
2
Total Second Floor
170.4
Furnace Location in Basement
Bedroom 3
Garage
“Jones” family reports
comfort is improved, but
still not well balanced
Total Main Floor
219

## Slide 10: “Jones” Home – Reasonably Balanced
Living Room
Family Room
Dining Room
Kitchen
Mud Room
Foyer
Bedroom 1
Bedroom 2
MBR
Bath
WIC
M. Bath
Bedroom 3
Garage
Total Second Floor
172
Air Handler Total Flow
610 CFM (1036 m3/hr)
Static Pressure in Supply Plenum
0.10 in W.C. (24 Pa)
38
39
23
28
30
10
2
2
Total Main Floor
180
30
25
32
15
12
29
9
28
Furnace Location in Basement
“Jones” family reports a
significant improvement in
comfort: “very well balanced”
Notes: Homeowner has used an electric blanket in the master suite since 2009. He said now they “turn on our electric blankets for comfort, but regret it later as it quickly gets too warm. That didn’t happen before.”

## Slide 11: Measurement Tools
How good does a hood need to be to get the job done?
  Accuracy
  Insertion Loss

## Slide 12: What is Accuracy?
measurement accuracy: closeness of agreement between a measured quantity value and a true quantity value of a measurand -- JCGM 200:2012

## Slide 13: What is Insertion Loss?
insertion loss: in telecommunications, insertion loss is the loss of signal power resulting from the insertion of a device in a transmission line or optical fiber and is usually expressed in decibels
  - Wikipedia
insertion loss: the change in the value of a physical parameter being measured due to insertion of the device used to measure it.
  - Steven Rogers

## Slide 14: Insertion Loss Example
When you insert a “cold” meat thermometer, it lowers the temperature of the meat.
How much?
  in a 5 lb (2.5kg) roast ?
  In a 4 oz. (113g) hamburger patty?
  In a ½ oz. (15g) slice of bacon?
Similarly…how much does a flow hood change the flow you’re measuring?

## Slide 15: Experimental Setup
Flow Metering Fan
Calibrated to 1%
Manometers for Pressure and Flow Measurements
Fan Controller – constant total flow, simulates ECM
Data Acquisition Computer
Iris Damper / Orifice Meter x4
Calibrated to 2%
Interchangeable Supply Register x4
Total System Leakage < 1 CFM with Plenum Pressure @ 0.2 in W.C. (50 Pa)

## Slide 16: Experimental Setup
Measure Accuracy and Insertion Loss Separately
Simulates residential ‘trunk and branch’ duct system
Orifice meters: flow measurement through all 4 branches
Orifice meters calibrated within 1% vs. metering fan
Flow metering fan calibrated 1%
Orifices adjusted to create trunk pressure of ~ 0.2 inH2O (50 Pa)
Fan maintains constant total flow (similar to ECM blower)

## Slide 17: Six Hoods Evaluated
Hood A:
Standard
24” x 24”
Pitot Array
Passive
Hood C:
Small Size
16” x 16”
Pitot Array
Passive
Hood D:
Small Size
16” x 16”
Pitot Array
Powered
Hood E:
Small Size
16” x 16”
Fan RPM
Powered
Hood F:
Standard
24” x 24”
Rotating Vane Anemometer
Passive
Hood B:
Small Size
13” x 13”
Rotating Vane Anemometer
Passive

## Slide 18: Four Supply Registers Evaluated
4 x 12 inch - 2 Way
. (100 x 300mm)
4 x 12 inch - 3 Way
. (100 x 300mm)
2 x 12 inch - 2 Way
. (50 x 300mm)
2 inch Jet
(50 mm)

## Slide 19: 6 Orientations of Hood over Register
□ = Centered
◇ = Top Edge
+ = 45 degrees
✕ = Top Corner
△ = Side Edge
✕ = Bottom Corner

## Slide 20
Chart: 4 x 12 inch 2-Way at 100 CFM (170 m3/h)
| 99.493361237096764 | 99.195858381978681 | 99.285770610415824 | 99.342776492612515 | 99.717161307300842 | 99.533052340667922 | 99.411014128296756 | 99.432558304335444 | 99.94427073132222 | 99.390730409608864 | 99.856999381959596 | 99.650767084553408 | 100.12041976487723 | 99.753140166804641 | 99.576475167669955 | 98.209882604347271 | 98.234730465692053 | 98.419423305357839 | 98.031305539397067 | 98.37891478117902 | 98.560980315069429 | 99.475048022314837 | 68.161586217586233 | 70.200890653876812 | 68.923523569034003 | 99.512090170002296 | 97.310399239091453 | 95.875715610417274 | 97.109192855023281 | 97.759912870634381 | 99.956550000000036 | 96.961008620689668 | 96.614123728813581 | 97.126286440677987 | 96.649450000000016 | 96.656931034482753 | 97.066096551724144 | 96.5 | 102.5 | 102.5 | 96.5 | 96.5
Hood D* | 0.012078 | 0.012831 | 0.010114 | 0.011573 | 0.011512 | 0.012156
Hood A | 0.16065 | 0.1168 | 0.23176 | 0.18414 | 0.26847 | 0.24307
Hood C | -0.083595 | -0.032929 | -0.085546 | -0.051323 | -0.06484 | -0.08686
Hood B | 0.044809 | 0.010248 | 0.046121
Hood E* | 0.022352 | 0.027377 | 0.014327 | 0.0075752
Hood F | -0.10273 | -0.08916 | 0.029587 | 0.003627 | -0.017142 | -0.093401
3% Error | 0.03 | 0.03 | -0.03 | -0.03 | 0.03
ACCURACY
INSERTION LOSS

## Slide 21
Chart: 2 x 12 inch 2-Way at 50 CFM (85 m3/h)
| 49.682157581984953 | 49.557725980030305 | 50.276108852235204 | 49.75810154221297 | 50.08323210638023 | 50.106067932964159 | 49.688324545322295 | 49.985600517961728 | 50.305105169490894 | 50.299695099840676 | 50.10252429433794 | 50.358366402085352 | 50.40666858153368 | 50.351390938673077 | 49.875492429288784 | 50.018638694156635 | 49.648779211816894 | 50.042949880307475 | 49.770793273176132 | 49.774422922448601 | 50.078838624256605 | 49.920152480631899 | 35.540835870667983 | 36.346857118753526 | 0 | 0 | 0 | 35.948123804149617 | 49.94670959427178 | 49.707662146901242 | 48.898059415505152 | 49.640898118587607 | 48.949684350288422 | 49.263964530684397 | 50.207880799206045 | 50.08391348563557 | 48.853233419011381 | 48.904351266300885 | 49.052743714092628 | 48.958454769466094 | 48.630646350912116 | 49.006420100226087 | 48.5 | 51.5 | 51.5 | 48.5 | 48.5
Hood D* | 0.03675 | 0.036088 | 0.036135 | 0.037483 | 0.036289 | 0.035275
Hood A | 0.42331 | 0.30219 | 0.29734 | 0.26891 | 0.37879 | 0.35845
Hood C | -0.16031 | -0.073492 | -0.10077 | -0.035579 | -0.05574 | -0.16132
Hood B | 0.10859 | 0.1084 | 0.12617
Hood E* | 0.030429 | 0.041246 | 0.050936 | 0.052624 | 0.056505 | 0.04194
Hood F | -0.15317 | -0.053352 | 0.24499 | -0.094636 | 0.012741 | -0.035224
3% Error | 0.03 | 0.03 | -0.03 | -0.03 | 0.03

## Slide 22
Chart: 4 x 12 inch 3-Way at 100 CFM (170 m3/h)
| 99.370628345405862 | 99.789785748072376 | 100.65280453122618 | 99.883761563306862 | 100.91240014357672 | 100.27982624454056 | 100.4438537076107 | 99.244586624153101 | 99.78034865996392 | 99.957243315715729 | 99.95798472748649 | 100.47188457722915 | 99.836667323205887 | 99.984316026734717 | 99.64983598869361 | 99.36084284128971 | 99.373016000946265 | 99.145746629888777 | 99.25521409960588 | 98.791007440132873 | 99.10992663614438 | 99.509532098701456 | 69.955007556419289 | 71.350580586464275 | 0 | 0 | 0 | 71.498704681039655 | 99.455606863917836 | 99.185199369288938 | 98.400020909092035 | 98.805573741987359 | 98.749882630444375 | 97.790561511133689 | 98.665854357552405 | 99.136466081156556 | 97.061534929330989 | 97.658576110181272 | 96.809413642141038 | 96.643307841139446 | 96.763777034667058 | 97.124826723493101 | 96.5 | 102.5 | 102.5 | 96.5 | 96.5
Hood D* | 0.014177 | 0.012957 | 0.013603 | 0.01382 | 0.013441 | 0.013093
Hood A | 0.20865 | 0.13449 | 0.1865 | 0.18939 | 0.23902 | 0.15018
Hood C | -0.064018 | -0.044006 | -0.051901 | -0.022721 | -0.018129 | -0.061648
Hood B | 0.046184 | 0.029863 | 0.019464
Hood E* | -0.028553 | -0.0073879 | 0.023829 | 0.0064515 | 0.016325 | 0.016294
Hood F | -0.066361 | 0.048966 | -0.053755 | -0.062321 | 0.0077682 | -0.12782
3% Error | 0.03 | 0.03 | -0.03 | -0.03 | 0.03

## Slide 23
Chart: 2 inch Jet at 50 CFM (85 m3/h)
| 51.367352132806161 | 52.780283423294691 | 52.218258896752666 | 51.728515997120617 | 51.090595676312454 | 51.226162216532849 | 52.828168990497453 | 50.917385716646812 | 51.473711177767179 | 51.428614775464034 | 51.352036960507242 | 51.289619151135788 | 51.03710300218917 | 51.413018625335233 | 50.963189826209906 | 52.306502379396896 | 52.19083494157919 | 51.403211691447844 | 51.269695645034496 | 51.159866930603073 | 52.301100298532099 | 50.928520654912539 | 54.606182790344327 | 49.910168364813231 | 49.328538571561069 | 49.271531502431309 | 48.989850484518449 | 53.932876573032452 | 50.989131103622491 | 50.950862488825386 | 50.459575129547872 | 50.768049105208256 | 50.471143446789945 | 50.730235151434165 | 50.867392134131137 | 49.332713528330878 | 49.119311026913792 | 48.418537539415837 | 48.050276081400135 | 48.658815974654495 | 48.83495099604086 | 50.460996025424201 | 50.900875112989354 | 54.756988696870302 | 53.764047392104146 | 52.226739459006147 | 53.576096927881231 | 52.125223629802214 | 53.609154259667541 | 48.5 | 51.5 | 51.5 | 48.5 | 48.5
Hood D* | -0.0066407 | -0.012335 | 0.020764 | -0.0039657 | -0.003021 | 0.0015874
Hood A | 0.57362 | 0.58861 | 2.1216 | 2.1468 | 2.4073 | 0.60854
Hood C | 0.41474 | -0.61679 | -0.20238 | -0.62941 | -0.58952 | 0.434
Hood B | 0.14543 | 0.089402 | 0.09426 | 0.093527 | 0.065634 | 0.13051
Hood E* | -0.62785 | -0.073354 | -0.058224 | -0.056782 | -0.0054859 | -0.42818
Hood F | 0.10293 | -0.65416 | -0.40552 | -0.65587 | -0.41507 | 0.073606

3% Error | 0.03 | 0.03 | -0.03 | -0.03 | 0.03
Different Scale

## Slide 24: Are Good Accuracy and Low Insertion Loss both required?
Accuracy Depends on
  Style of Hood
  Position on the Register
  Style of Diffuser
Insertion Loss Depends on
  Flow Rate - highly dependent
  Style and size of Hood
  Hood Loss relative to parallel paths
  Hood Loss relative to series paths
YES, you need both to effectively balance an HVAC system

## Slide 25: Conclusion – What the Data Says
Accuracy Errors: 15% - 50% were common
  Standard 24 x 24 inch (610 x 610 mm) passive hood not suited for residential applications
Insertion Loss Errors: 30% in one case
Orientation of the hood: 15 – 20% variation was common
Powered flow hoods: more accurate, smaller insertion loss
Notes: Powered hood accuracy is a result of flow conditioning, which is only possible with a fan to compensate for the pressure loss.

## Slide 26: Conclusion – What it means
Comfort problems abound in residential HVAC and most are difficult to diagnose without knowing air flows from each supply register
Balancing is easier and requires less precision in buildings that are better insulated and more air tight
Many air flow hoods may not be accurate enough for applications that are more challenging to balance – poorly insulated and/or leaky envelopes

## Slide 27: Questions
E-mail: srogers@energyconservatory.com