YEA meeting TC1.11 – June 24, 2024

Begin at 3:30pm Eastern

Nick – intros (in the room and online)

Reviewed the TC bylaws and TC roles and responsibilities

Abdur – VFDs and Motors 101 Program Submission overview

- NEMA drive enclosure types

- VFD bypass options and system redundancy

- VFD filtering and harmonic mitigation

- VFD motor cable considerations

- VFD harmonic analysis and selection

Watch out for NEMA 4 indoor vs. NEMA 4 outdoor in specifying

Motor starting types – open discussion

Michael Lyda – shared motor starting videos: Power Quality Videos - YouTube

Nick – star/delta motor starting

VFD filter techniques – Line reactors, Passive/Active filtering at the drive, system level filtering

Advanced VFD Technologies like 12-pulse, 18-pulse, 24-pulse, Active Front End, or Matrix Converter technology all inherently minimize harmonic distortion

VFD Sizing and Motor Compatibility

Size based on motor amperage, not just horsepower. Mismatched sizing leads to overheating and premature failure

Electronically Commutated Motors (ECM) – have built in control so not compatible with external VFD

Permanent Magnet (PM) motors – may require special VFDs due to back EMF from rotor magnets

Need to add motor efficiency and new motor types to ASHRAE Handbook 45

Regenerative drives – open discussion, not as common with fan applications

Communication and Control Considerations

- Control types: BACnet, Modbus, Profibus, N2

- Match communication protocol to Building Automation System (BAS)

- Wiring and I/O requirements – digital and analog inputs, analog outputs

Conclusions – VFDs offer significant benefits; Energy Efficiency, Soft Starts, Improved Comfort

David Nowak – motion to end meeting, Ken Fonstad – second that motion

End at 5:29pm Eastern