## Slide 1
Effective Energy Management in New and Existing Buildings
Richard J. Pearson, P.E., ASHRAE Fellow
June 22, 2019
Notes: Thank you very much. This presentation, first delivered at the Winter Meeting in January 2010, was prepared with help from TC committee.
This presentation is available in abridged version 1 hour for presentation at ASHRAE chapter meetings.
It is based on a three-hour version developed and presented at ASHRAE meetings and conferences.
We have updated slides that refer to DoE data, some details and screen shots of ENERGY STAR Portfolio Manager and several of the course examples and confirmed that web references are still validdicd.
1

## Slide 2: Copyright
Copyright  2017 by ASHRAE. All rights reserved. No part of this presentation may be reproduced without written permission from ASHRAE, nor may any part of this presentation be reproduced, stored in a retrieval system or transmitted in any form or by any means (electronic, photocopying, recording, or other) without written permission from ASHRAE.
ASHRAE has compiled this presentation with care, but ASHRAE has not investigated and ASHRAE expressly disclaims any duty to investigate any product, service, process, procedure, design or the like, that may be described herein. The appearance of any technical data or editorial material in this presentation does not constitute endorsement, warranty or guaranty by ASHRAE of any product, service, process, procedure, design or the like. ASHRAE does not warrant that the information in this publication is free of errors. The user assumes the entire risk of the use of the use of any information in this presentation.
Notes: ASHRAE has compiled this presentation with care, but ASHRAE has not investigated and ASHRAE expressly disclaims any duty to investigate any product, service, process, procedure, design or the like, that may be described herein. The appearance of any technical data or editorial material in this presentation does not constitute endorsement, warranty or guaranty by ASHRAE of any product, service, process, procedure, design or the like. ASHRAE does not warrant that the information in this publication is free of errors. The user assumes the entire risk of the use of any information in this presentation.
Comments, criticism and suggestions regarding the subject matter are invited. Any errors or omissions in the data should be brought to the attention of Martin Kraft, Managing Editor.
ASHRAE Learning Institute:
Karen Murray, Manager of Professional Development
Sarah Boyle, Managing Editor
Kelly Arnold, Administrative Assistant
For course information or to order additional materials, please contact:
ASHRAE Learning Institute
1791 Tullie Circle NE
Atlanta, GA 30329
Telephone: 404-636-8400
Fax: 404-321-5478
Email: edu@ashrae.org

## Slide 3: AIA/CES Registered Provider
ASHRAE is a Registered Provider with The American Institute of Architects Continuing Education Systems. Credit earned on completion of this program will be reported to CES Records for AIA members. Certificates of Attendance for non-AIA members are available on request.
This program is registered with the AIA/CES for continuing professional education. As such, it does not include content that may be deemed or construed to be an approval or endorsement by the AIA of any material of construction or any method or manner of handling, using, distributing, or dealing in any material or product. Questions related to specific materials, methods, and services will be addressed at the conclusion of this presentation.

## Slide 4
GBCI cannot guarantee that course sessions will be delivered to you as submitted to GBCI. However, any course found to be in violation of the standards of the program, or otherwise contrary to the mission of GBCI, shall be removed. Your course evaluations will help us uphold these standards.
Course ID: 90009942
Effective Energy Management in New & Existing Buildings
By ASHRAE
Approved for:
6
General CE hours
0
LEED-specific hours

## Slide 5: Today’s Audience
People responsible for facility management inside their organization
Consulting engineers who provide energy management services to facilities
Engineers who provide advice on energy management to facility managers and staff
Vendors selling products to facilities
Notes: We typically find the audience consists of different segments.
WE EXPECT PARTICIPANTS TO ACTUALLY GO DO SOMETHING DIFFERENT IN THEIR BUILDINGS NEXT WEEK TO USE ENERGY MORE INTELLIGENTLY.
The course is aimed at facility managers who are usually too busy to attend!
Designers, contractors and vendors can benefit—not rocket science, these people can assist facility managers and perhaps sell services. As you work with the information, including the exercises, think about how you can help your clients become better energy managers.
NOTE: first two audience sectors are DO-ERS; third sector is ADVISOR or COACH or INFLUENCER.
For all sectors, we emphasize MANAGEMENT as the key activity discussed in this seminar, not application of technical engineering expertise nor deep discussion of technical aspects of energy end use equipment or design.
We will present case examples and provide practice with fundamental ingredients necessary for Energy Management.

## Slide 6: Course Objectives
Describe the ENERGY STAR® management cycle
Analyze basic billing and load profile information
Distinguish the levels I, II and III of a commercial building energy audit
Identify opportunities for energy savings in your buildings based on course suggestions
Develop an action plan to get started, targeting:
  Preliminary energy analysis or
  A test of discretionary facility operation.
Notes: The aim of this course is to provide enough information to inspire you to take action when you return to work next week. You can start to apply the basics of energy management even if your organization does not have a formal program yet; or you can apply insights from the seminar to energy management activities already in place.

## Slide 7
Guides for Today’s Seminar
ENERGY STAR Guidelines for Energy Management
Connections:
ASHRAE Standard 100-2018, Energy Efficiency in Existing Buildings
ASHRAE Standard 211-2018, Standard for Commercial Building Energy Audits
2015 ASHRAE Handbook—HVAC Applications, Chapter 36
Practical experience
Opportunities in your buildings
Notes: www.energystar.gov
We need a map because the journey has many interesting sights and places to visit and we want to stay on track.
The ENERGY STAR website has tools and links to many useful sources. THERE IS AN IMPLICIT FOCUS ON CAPITAL PROJECTS TO IMPROVE ENERGY USE. However, the cycle here applies to our focus on operations excellence, too.
The main steps are good advice and the idea of a cycle that continues to repeat is critical
THE ACTUAL DETAILS AND ADVICE in the steps presume a commitment to a specific “big agreement” to manage in a particular way. This commitment can be BUILT by preliminary cycling through the process, it does not need to rise or fall on whether the senior management make a formal commitment and issue a detailed energy policy before you can begin.
You can build WILL that eventually gets expressed as formal organizational commitment but if we hold out for the ENERGY STAR details at Make the Commitment stage, we are cutting off too many opportunities.
In any event, many senior managers will want a lot more evidence of “what’s in it for our organization” before committing to the formality described by ENERGY STAR; the formality can EMERGE from the specifics of the organization’s management approach and norms.

## Slide 8: Today’s Topics
Introduction to energy management
Why commit to energy management?
Assessing performance and setting goals
Action plans: ideas and a test method
Evaluating results
Energy management summary
What can you do, starting next week?
Notes: We will key our slides to the first six topics. Topic 7 takes the form of a planning exercise, near the end of the seminar.

## Slide 9
“Discomfort is Expensive”
Action Plans: Ideas and a Test Method

## Slide 10
For Example…
If typical office building includes one person for every 300 ft2
And the annual utility cost is $2 per ft2
Then each person is “responsible” for $600 per year
If dramatic energy conservation reduces energy usage by 50%, or $1 per ft2
Then savings per person = $300 per year
If average worker salary is $50,000/yr
Then savings per person = $300/$50,000 = 0.6%
Therefore any level of discomfort that distracts a person will clearly cost more in lost productivity than the $300 savings in energy
Action Plans: Ideas and a Test Method

## Slide 11: Introduction to Energy Management
Introduction to Energy Management
Notes: This section provides an overview of the basic ingredients of energy management.

## Slide 12
12
Energy Management 101—Example
Management commitment
Manual daily meter reading
Operational changes only
33% energy savings in 12 months
Introduction to Energy Management
Notes: This photo was from a 35mm slide for an ASHRAE presentation in 1978. Building built in 1970’s—the example is still relevant, for even as technology advances, the basic things the manager did are still pertinent to this subject.
12

## Slide 13
13
Energy Management 101 The Building
20-story office building:
200,000 ft2
Five years old, no energy conservation
Complex, energy intensive HVAC systems
High utility bills
No building automation system
Introduction to Energy Management
Notes: Instructor reads slide points.
13

## Slide 14
14
Energy Management 101 How It Worked
Actions by facility manager:
Reviewed operations ideas with building engineer and design engineer
Reviewed daily meter data for impact, intuitively adjusting for weather
Harassed/complimented building engineer daily on performance
Introduction to Energy Management
Notes: The facility manager got the engineers to review the utility bills and sat in on the meeting—they argued on technical issues, no progress.
Then he changed his approach using the REVIEW and HARASS
The talking that led nowhere was replaced by an action plan.
14

## Slide 15
15
Energy Management 101 How It Worked
Actions by building engineer
Aligned building schedules with occupancy times
Raised cold deck temperature
Lowered hot deck temperature
Outdoor air was introduced only during occupied hours
Reduced duct pressures
Introduction to Energy Management
Savings in one year: 33%!
Notes: The building engineer realized he was being watched with real data. He started to adjust everything he could find. As he applied himself in a skilled way, he got the bottom line.
This was done with pneumatic controls and manual data collection.
THE KEY POINT: These energy savings actions would not have taken place without the management oversight.
15

## Slide 16: Here’s a Word About Capital Projects
  Energy management is the foundation for effective capital upgrades:
    Measure performance
    Monitor performance over time
    Deploy operations changes along with new equipment to get greatest bang for buck
Introduction to Energy Management
Notes: Energy management as presented in this seminar stresses skills and action to
Measure performance
Monitor performance over time to catch problems and gain insights
Make operations changes to fine tune energy use.
If you have this kind of energy management, you will be able to check performance of upgrades and adjust (or correct) problems in ways that minimize cost and waste.
Note that many descriptions of energy management emphasize capital projects, including what you will find on the ENERGY STAR website. We will not emphasize capital projects today.

## Slide 17
www.energystar.gov
ENERGY STAR guidelines
describe a management cycle that helps you with execution—getting things done!
The Management Content of Energy Management
Introduction to Energy Management
Notes: We have added the accountability box and feedback loop. It is important! This is why the EM 101 worked. It is implied in the flowchart but we highlight to move from a theoretical subject to a practical subject that makes a difference.

## Slide 18
Energy Manager Job Description
Chapter 36, 2015 ASHRAE Handbook— HVAC Applications
Functions
  Technical
  Policy related
  Planning and purchasing
Qualifications
  General
  Educational/professional
Introduction to Energy Management
Notes: In chap 35 of the ASHRAE Handbook, there is a thorough description of the energy manager’s job description.
The chapter describes information about purchasing of energy and how to handle additional resource management, like fleet fuel and water.

## Slide 19
Job Description—Purchasing
Lower-cost energy
Other non-building utilities
  Vehicle fuel
  Water
Introduction to Energy Management
Notes: In chap 35 of the ASHRAE Handbook, there is a thorough description of the energy manager’s job description.
The chapter describes information about purchasing of energy and how to handle additional resource management, like fleet fuel and water.

## Slide 20
20
Headquarters in Fond du Lac, Wisconsin
Manufacturing and sales organization
Multiple facilities across the U.S.
Multimillion dollar utility bill
Jerry Eaton—energy manager
>$1 million annual savings (>5% of bills)
Jerry Eaton’s
Story
Introduction to Energy Management
Notes: This story describes in greater depth the management ingredients of Energy Management, applied to a manufacturing company.
20

## Slide 21
21
Jerry Eaton’s Discoveries
Utility cost was an overhead item—not a manageable expense
Stickers on light switches—no impact on expense or consumption
Introduction to Energy Management
Notes: The company paid for the utility costs but no one had the costs in their department budget to understand, track and control.
The efforts to control costs were diffuse and disconnected from day to day management actions—signs,posters and reminders by themselves typically do little to affect energy use and may in fact promote cynicism among staff who may see wasted energy and realize no one in authority is paying attention to change the situation.
21

## Slide 22
22
Jerry Eaton’s Parallel Activities
Developed a corporate-wide chain of accountability:
  Began with buildings (each with a meter)
  Then departments within buildings (each with a meter)
  Appointed a person in each location to be responsible for proven results
Introduction to Energy Management
Notes: The intervention is NOT about installing meters. It is about having people engage with energy information about chunks of the organization that provide the basis for action.
Nonetheless, properly used, proper metering provides the data for real improvements. The company invested a lot in metering, and then used that investment.
MORE ON METERING
Buildings are a natural unit that may already have meters that can be read. Stand-alone electrical meters can be installed for less than $1000 on service panels if the utility does not have a revenue meter already in place. Electric meters tied into the facility control system typically will cost more for the convenience of common collection of data.
Gas meters typically are more expensive to install for the customer; like Jerry, you may start with electric metering.
Mercury Marine has large facilities with multiple electrical service panels within them. Where it makes sense, you can install meters to track energy use by area within a building.
With the information provided by the meters, you need a person who will have to stand up and be counted on progress (or lack therof) to use energy more intelligently.
22

## Slide 23
23
Developed an accountability process to review results regularly
Typical monthly agenda:
A look back
  - Submeter data review, check impact of last month’s action ideas
A look forward
  - Brainstorm ideas to decrease energy
  - Commit to try ideas (who, when)
Picture of meeting
Jerry Eaton’s Parallel Activities
Introduction to Energy Management
Notes:   An annual review by itself is not frequent enough.
  A monthly interval is reasonably functional
    Matches typical interval of utility bills
    Provides time to try out ideas
    Downside: prep for the meeting comes just before the meeting, leaving 3 weeks a month without action.
  Some type of weekly review has proven to be very effective.
23

## Slide 24
Installed
Submeters and
Procedures
Established
Reviews
Found
Waste
Reduced
Waste
Established
Budget
Accountability
Established
Building
Energy
Teams
Jerry Eaton’s Parallel Activities: Summary
Introduction to Energy Management
Notes: Jerry did these things:
Developed a significant sub-metering program
Developed procedures to monitor the meters on a regular basis—more than once a month.
The procedures specified WHO was to do the monitoring and HOW to do it.
These two basic components enabled Jerry and the staff to identify wasted use of energy and then act to reduce the waste.
OPPORTUNITY TO LINK ENERGY MANAGEMENT TO YOUR ORGANIZATION: if your organization is working on LEAN management, use the language of WASTE to connect to managers when discussing energy management.

## Slide 25
25
Jerry Eaton’s Success Story
The cost of energy became real for each unit
Energy teams, by building or department
The “buck” stopped at one person in each department
Annual savings: over $1 million (>5%)
Introduction to Energy Management
Notes: This slide summarizes the management changes in the energy management system at Mercury marine.
The cost of energy ceased to be an overhead item: Buildings and departments had annual budgets increased by approximately the amount of the cost of energy attributable to each entity.
Energy teams were developed in each entity, coordinated by the energy manager.
The “buck” stopped at one person in each entity, who received regular data from ongoing monitoring and measuring performed by the energy manager.
25

## Slide 26
26
Meters and
Submeters
Meters by themselves do not save anything
No direct payback on the purchase of a meter
That is not the basis for their justification as an energy conservation investment
Question: How can you manage it if you can’t measure it?
Introduction to Energy Management
Notes: This slide summarizes the management changes in the energy management system at Mercury marine.
The cost of energy ceased to be an overhead item: Buildings and departments had annual budgets increased by approximately the amount of the cost of energy attributable to each entity.
Energy teams were developed in each entity, coordinated by the energy manager.
The “buck” stopped at one person in each entity, who received regular data from ongoing monitoring and measuring performed by the energy manager.
26

## Slide 27
27
Measurement Technology
Measurement technology is continuously improving and becoming more affordable
More than one way to develop measurements that are useful in an energy management program
Creative thinking and competitive bidding can produce surprising results
Introduction to Energy Management
Notes: This slide summarizes the management changes in the energy management system at Mercury marine.
The cost of energy ceased to be an overhead item: Buildings and departments had annual budgets increased by approximately the amount of the cost of energy attributable to each entity.
Energy teams were developed in each entity, coordinated by the energy manager.
The “buck” stopped at one person in each entity, who received regular data from ongoing monitoring and measuring performed by the energy manager.
27

## Slide 28: Was Jerry Eaton Really an Energy Manager?
Authority to manage energy?
Responsibility?
Accountability?
Introduction to Energy Management
Notes: A title on a business card is not enough—we define the role of manager in these terms:
Authority is the right to take action (or delegate the action) to manage energy.
Responsibility is the obligation to make sure the actions are done to manage energy.
Accountability means Jerry owned the results of the actions to manage energy (good, bad or not done at all.)
What’s your assessment based on our story?
Accountability is such a key piece of the puzzle that we amended the ENERGY STAR Management cycle. If the results of the actions don’t matter to the boss, that’s a practical sign of low commitment and a predictor that not much will happen—you will look back after a few months and energy use, habits and practices will be pretty much unchanged.

## Slide 29
ENERGY STAR Guidelines for Energy Management
www.energystar.gov
Introduction to Energy Management
!
Notes: The Jerry Eaton story makes the case for showing the Accountability Loop—between the executive or manager making the commitment and the person reporting on progress.
If you want a strong clue to whether management has made an effective commitment to energy management: find out who is ACCOUNTABLE for reviewing energy use and improving perfomance.
If NO ONE is accountable, then energy policy statements and other signs of management intent are preliminary.

## Slide 30: Exercise 1: Energy Management Assessment
Introduction to Energy Management
Page 3
in the exercises
Notes: Turn to the Supplementary Exercise Packet. We list 14 Exercises. We will go through most of the exercises ; if we have time, we will go through all of them.
Please turn to the Management Assessment Exercise on page 3. We’ll give you a few minutes to work through the checklist, for a building you know.
The checklist focuses on the accountability ingredients featured in the Jerry Eaton story.
ENERGY STAR provides Assessment Matrices that help you to evaluate your Energy Management system with specific reference to the ENERGY STAR Energy Management cycle. You may find these matrices useful after you become familiar with the Energy Management cycle.
http://www.energystar.gov/index.cfm?c=guidelines.guidelines_index
DEBRIEF:
Ask how many buildings have less than 5 YES checked. TYPICAL!
Ask how many buildings are 5 or more but less than 10 GOOD BASIS TO DO MORE—ask: are the YES mostly about monitoring?
Ask how many buildings are more than 10 but less than 17 ASK FOR STORIES FROM ONE OR MORE PARTICIPANTS ABOUT WHAT WORKS WELL IN THEIR MANAGEMENT SYSTEM.
Ask how many buildings are 17 or more. WE DON’T EXPECT ANYONE TO SCORE A BUILDING THAT HIGH BUT IF THERE IS A SCORE, ASK ABOUT THEIR EXPERIENCE AND WHAT THEY EXPECT TO LEARN TODAY.

## Slide 31: Why Commit to Energy Management?
Why Commit to Energy Management?
Notes: You can use the following 12 slides to present to managers or Energy Teams or Sustainability teams back home. The slides give the big picture about energy use in buildings. The information in the slides can help foster the will to tackle sustained energy management in your organization.

## Slide 32
32
ENERGY STAR Guidelines for Energy Management
www.energystar.gov
Why Commit to Energy Management?
Notes: Let’s talk about commitment.
The ENERGY STAR website recommends that your organization needs to create a formal energy policy and to create an energy team. This is particularly important in the context of capital projects, a dominant perspective on the ENERGY STAR site.
As we noted in the previous section, we believe that a practical test of commitment is whether the organization has appointed some PERSON who is accountable for energy performance and improvement. That’s why we have added the accountabilty loop, that connects “make the commitment” and “Evaluate progress.”
If your organization already has an energy policy, then find it and read it.
How well is the policy being followed? You have ways to judge, using the scoring checklist we used a few minutes ago in the first exercise.
If your organization has not yet made the formal commitment and wants to gain some experience with energy management, that’s great! You can still get started!
You can demonstrate the value of energy management with targeted examples in your own buildings that help make the case for sustained energy management—building the will to make a formal commitment in terms of policies AND in terms of assigning people to be accountable.
32

## Slide 33
33
ENERGY STAR Guidelines for Energy Management
https://www.energystar.gov/sites/default/files/buildings/tools/Guidelines%20for%20Energy%20Management%206_2013.pdf.
Why Commit to Energy Management?
Notes: Let’s talk about commitment.
The ENERGY STAR website recommends that your organization needs to create a formal energy policy and to create an energy team. This is particularly important in the context of capital projects, a dominant perspective on the ENERGY STAR site.
As we noted in the previous section, we believe that a practical test of commitment is whether the organization has appointed some PERSON who is accountable for energy performance and improvement. That’s why we have added the accountabilty loop, that connects “make the commitment” and “Evaluate progress.”
If your organization already has an energy policy, then find it and read it.
How well is the policy being followed? You have ways to judge, using the scoring checklist we used a few minutes ago in the first exercise.
If your organization has not yet made the formal commitment and wants to gain some experience with energy management, that’s great! You can still get started!
You can demonstrate the value of energy management with targeted examples in your own buildings that help make the case for sustained energy management—building the will to make a formal commitment in terms of policies AND in terms of assigning people to be accountable.
33

## Slide 34: Dollar Savings and Margin
$ 1,000,000 Revenue
$ 950,000 Expenses
$ 50,000 Margin (5% of revenue)
A cost savings of $1000 @ 5% margin
Equivalent to $20,000 in increased revenue
Why Commit to Energy Management?
Notes: Managers put numbers in context. Dollar numbers in organizations (not-for-profit as well as for profit) can be connected to revenue and expenses to gauge the dollar impact of energy savings.
Check the arithmetic to confirm the statement:
Increase revenue (and costs, proportionally) Maintain revenue (and decrease costs by $1000)
1,020,000 1,000,000
969,000 - 949,000
_________ ________
51,000 51,000
In this case, the revenue impact is a factor of 20.
ADDITIONAL EXAMPLE: The median total margin for U.S. Hospitals is 4%, so the “revenue impact factor” is at least 25 for half of U.S. hospitals
(source: http://www.squarefootage.net/download_presentation.htm presentation by B. Alan Whitson, "Making Sense Out of Sustainability in Healthcare" Chicago, July 31, 2009, IFMA Healthcare Council Seminar).
If your organization operates with low margins, energy savings that do not depend on capital investment are an especially attractive opportunity.

## Slide 35: Financial Value Tools from ENERGY STAR
Building Upgrade Value Calculator—Commercial Real Estate
Financial Value Calculator—Corporate Real Estate
Cash Flow Opportunity Calculator
Why Commit to Energy Management?
Notes: 35
RESOURCE: FINANCIAL VALUE TOOLS
The Building Upgrade Value Calculator estimates the financial impact of proposed investments in energy efficiency in office properties. The calculations are based on data input by the user, representing scenarios and conditions present at their properties. Required inputs are limited to general characteristics of the building, plus information on the proposed investments in energy efficiency upgrades
The Financial Value Calculator tool uses the prevailing price/earnings ratio to estimate the market value of increased earnings that can result from increased energy efficiency. The tool uses the corporate data you enter to calculate your company’s potential financial returns. Both publicly- and privately-held companies can use the FVC to assess the potential value of improved energy performance.
The Cash Flow Opportunity Calculator can accelerate the installation of energy efficiency projects by addressing three critical questions about implementing these projects;
1) How much new energy efficiency equipment can be purchased from the anticipated savings?
2) Should this equipment purchase be financed now or is it better to wait and use cash from a future budget? (avoid paying interest)
3) Is money being lost by waiting for a lower interest rate?
http://www.energystar.gov/index.cfm?c=assess_value.financial_tools

## Slide 36: Where Do We Use Energy?
Why Commit to Energy Management?
Source: U.S. EIA.
Notes: In this seminar, we are going to tackle energy use in buildings, there are also energy management opportunities in transportation and industrial sectors.
Source: 2008 Annual Energy Review, http://www.eia.gov/FTPROOT/multifuel/038408.pdf Figure 1.0

## Slide 37: Renewable Energy Sources
Source: U.S. EIA.
.

## Slide 38
Energy Management Potential
Why Commit to Energy Management?
Buildings consume 40% of U.S. energy
  Residential (21.0%) + Commercial (18.7%) = 39.7%
33% reduction of building energy is possible
  39.7% × 33% = 13.1%
This will save 13% of U.S. energy!
Notes: We believe it is economically feasible to reduce energy use by 33% , not every building but in a portfolio of buildings, on average.
33% reduction of 39% of U.S. Energy= 13% savings potential FOR RESIDENTIAL AND COMMERCIAL.
The arithmetic in this slide derives from 2006 statistics. The near term forecasts do not change the story.

## Slide 39: Renewables as an Environmental Solution?
Why Commit to Energy Management?
Source: U.S. EIA.
.
.
Notes: Here are the sources of energy in 2008 in the US. You can see at a glance that renewable energy is a small piece of the Energy Pie.
(source: Table 1.3 ”Primary Energy Consumption by Source, 1949-2009” Annual Energy Overview, http://www.eia.doe.gov/emeu/aer/overview.html)
The three largest components are fossil fuels, which when burned produce not only energy but greenhouse gases like carbon dioxide, CO2.
Fossil fuels dominate the present. Fossil fuels will dominate the next 20 years.
In this breakdown, Renewables excluding Hydro, is dominated by biomass, not PV and wind, the usual sources we think about when we hear the term “renewables.”
Renewables will not, in the short term, have much impact on climate and other environmental issues.
The mix of energy sources is not expected to change radically over the next few years.

## Slide 40
Energy Management is the Quickest, Cheapest, Cleanest Way to Extend World Energy Supplies
Why Commit to Energy Management?
Energy management can provide nearly two times
the environmental impact of renewable energy!
Notes: If you pull the information in the previous slides together, we get to this conclusion:
Energy Management is the Quickest, Cheapest, Cleanest Way to Extend World Energy Supplies.
Comparing the savings with renewable energy, the most effective thing we can do is attack wasted energy and save.
We are not denigrating renewable energy but rather observing that we have tremendous potential in the buildings we have.
Energy management implies you will learn how to use energy more intelligently in your buildings, reducing waste and assuring that changes to procedures and equipment yield their potential.
The 14% national impact provides an achievable percentage of energy savings from work with existing buildings, derived from our estimate of 33% savings in building energy use—though there are diminishing returns as you tackle opportunities (the first 5% is usually less costly than the last 5%).
Another way to look at the same figures: if you make more effective use of energy derived from fossil fuel, the % of the energy pie contributed by renewables goes up, even if no more renewable production is added. Reducing the use of fossil fuels increases the relative impact of renewables.

## Slide 42: Where Can You Get the 33%?
Some from smarter use of what you have right now
Some from capital upgrades
Why Commit to Energy Management?
Notes: The two ways to get the savings are managing what you have better (wringing out waste) and replacing equipment (HVAC systems, lighting, revised control systems, etc.)
This arithmetic applies to existing buildings, which is a huge opportunity. You hit design constraints and strong economic barriers beyond the level of 33%, with the current costs of energy and technology.
This seminar will focus on smarter use of the systems and technology you have right now, which can account for as much as half of the potential available savings at no or low cost.
Of course in any specific building, you may have more potential impact from smart use of what you have vs equipment changes or equipment may lead the way.

## Slide 43
Greener Pastures with Energy Savings
Emissions Reduction at Madison College
Why Commit to Energy Management?
Energy | Usage FY 01/02 1.2 Million ft² | Usage FY16/17 1.9 Million ft² | Annual Reduction!
Electricity | 23,000,000 kWh | 16,000,000 kWh | 7,000,000 kWh
Natural Gas | 900,000 therms | 400,000 therms | 500,000 therms
Emissions | Emissions FY 01/02 | Emissions FY 16/17 | Annual Reduction!
CO2 | 25,000 tons | 15,000 tons | 10,000 tons
The above energy savings were achieved with an additional 700,000 ft² conditioned space!
Source: Madison College Engineering Manager. Wesley Marquardt. wmarquardt@madisoncollege.edu.
Notes: This slide illustrates the conversion of energy savings into environmental impact.
You can convert savings of energy into emissions using factor tables produced by the EPA and the Department of Energy.
The calculations of emissions in this slide come from Emissions Factors and Energy Prices for the Cleaner and Greener Environmental Program
http://www.cleanerandgreener.org/download/efactors.pdf which has emissions factors by state.
Also, the EPA eGRID program has similar information, on a state by state and power plant basis, http://www.epa.gov/cleanenergy/energy-resources/egrid/index.html
ENERGY STAR’s Portfolio Manager on-line program will calculate the emissions for your buildings automatically so you can let ENERGY STAR do the emissions arithmetic for you! We’ll discuss the Portfolio Manager tool later this morning.
The impact on environmental emissions is impressive, equivalent to more than 800 kW of PV production in the upper Midwest.
MANAGEMENT NOTE: Wes reduced the energy use in the face of increased program demand and increased square footage.

## Slide 44
Greener Pastures with Energy Savings
Energy Cost Avoidance at Madison College

## Slide 45
ENERGY STAR—Carbon Emissions from Building Energy Use http://www.energystar.gov/index.cfm?c=evaluate_performance.bus_ portfoliomanager_carbon.
Carbon Emission eGrid Regions
Why Commit to Energy Management?

## Slide 46
AK, WA, WI Comparison
Reducing electric usage in WI can have a much greater impact on decreasing CO2 emissions than similar reduction measures in other parts of the country!
Why Commit to Energy Management?
State | Main Associated eGrid Region | CO2 Emission Rate (lb/MWh) per ENERGY STAR 2015 | Power Generation Notes
WI | MROE | 1,522.6 | 51% coal, 22% nuclear, 18% natural gas
WA | NWPP | 665.8 | 77% hydro, 8% nuclear, 6% wind
AK | AKMS | 481.2 | 52% natural gas, 23% hydro, 15% oil

## Slide 47
New Buildings Are a Target Too!
New buildings are often inefficient at start-up (even LEED-certified buildings).
New building performance significantly deteriorates in the first three years of operation, by as much as 30% (even those designed as energy-efficient green buildings).
Why Commit to Energy Management?
Notes: DICK Check Citation on deterioration in operation.
What about Commissioning? A good idea but not the whole story
LEED® buildings require commissioning before start-up as part of LEED certification
12-month review after occupancy has not been required by earlier versions of LEED (unless M&V point sought)—the new 3.0 version does require checking of energy use.
Retro-commissioning gets equipment working right in existing buildings,
  a good foundation for sustained energy management!
  There is a strong implication that LEED buildings use less energy (Platinum > Golg> Silver > Standard). LEED NC recognizes a DESIGN that should be energy efficient. Most LEED certifications in the past have not been followed by actual energy tracking and analysis of performance LEED EB does require tracking. And revisions to LEED NC suggest tracking will be required in the future.

## Slide 48
Why Commit to Energy Management?
GSA Energy Management Program
U.S. Courthouse
Jacksonville, Florida
Constructed in early 2000s
Disappointing energy use
DOE-ORNL Report

## Slide 49
We’ll come back to this example after we’ve defined a few terms…
Why Commit to Energy Management?
2000s New Building Performance
Far less efficient than design intent

## Slide 50: The Great Dane Case
Doty Street Pub
Hilldale Pub
Fitchburg Pub
www.greatdanepub.com
Why Commit to Energy Management?
Notes: The Great Dane is a small chain of brew pubs. They want to manage their use of energy better, as part of a larger commitment to sustainability.
Eliot Butler, President,
  Motivated to manage energy costs
  Looking at the big picture of sustainability
  Interested in getting more detailed look at energy use
Rob Wise, Facilities Manager
  is directed by Eliot to help the pubs use energy more wisely.
  Uses the local utility’s web site to view and study monthly energy use for the three sites.
  Understands the major uses of energy.
  Looking at equipment upgrades that save energy.
  We’ll use some of Great Dane’s data and actions to illustrate ideas during the seminar.

## Slide 51: Energy Management Status Spring 2008
Total: 5 YES 9 NO No bonus items
Why Commit to Energy Management?
Notes: The point of this slide is that there may be something already in place for Energy Management—just as we recommend taking a “try it on a limited scale” for changes to operating conditions (“learn by doing”), so too for upgrading the energy management at a facility.
In terms of the version of the Energy Management Checklist in Exercise 1, in Spring 2008 here is the Great Dane’s score:
5 YES 9 NO and no bonus points.
They will increase their score by the changes they will make, outlined in the exercises you’ll tackle.

## Slide 52: Background
Spring 2008: Eliot, the president, commits to work on energy management—learn by doing, test and adapt.
Rob, the facilities manager, will lead work through the ENERGY STAR cycle, assisted by a consultant, reporting monthly to Eliot on progress.
Practical commitment: facilities manager will work regularly on energy management, starting with assessment of performance, aiming to have impact within a few months.
Why Commit to Energy Management?
Notes: No formal energy policy written was created at the beginning—we believe actions speak louder than words, we started with simple actions that can inform the statement of energy policy that fits the organization.

## Slide 53
Assessing Performance
Assessing Performance and Setting Goals

## Slide 54
ENERGY STAR Guidelines for Energy Management
www.energystar.gov
Assessing Performance and Setting Goals
Notes: The ENERGY STAR flowchart gives good advice—you should have some idea of WHERE YOU ARE TODAY, what your performance is now—and to set some goals for progress—before you set to work.
In order to assess performance and set goals, you have to have meaningful measures of performance. This section of the seminar will present basic measures of energy use, beginning with the energy use available from monthly utility bills.
A common danger in improvement work is to get stuck in first stage of assessing performance.
As in most aspects of life, beware letting a drive for perfection in assembling and displaying performance data delay your efforts to begin effective changes (don’t let perfection be the enemy of the “good enough”).

## Slide 55: ENERGY STAR Advice: Assess Performance
Assessing performance is the periodic process of evaluating energy use and establishing a baseline.
Data collection and management
Baselining and benchmarking
Analysis and evaluation
Assessing Performance and Setting Goals
Notes: Assessing your energy performance helps you to:
Categorize current energy use by fuel type, operating division, facility, product line, etc.
Identify high performing facilities for recognition and replicable practices.
Prioritize poor performing facilities for immediate improvement.
Understand the contribution of energy expenditures to operating costs.
Develop a historical perspective and context for future actions and decisions.
Establish reference points for measuring and rewarding good performance
NOTE THAT THE ENERGY STAR ADVICE says that assessing performance is NOT A ONE TIME ACTION! Rather it is the periodic process (repeats over time, and there are steps to take).
To assess performance, you need to engage in three sets of activities:
Data Collection and Management—you gave to get the relevant data on energy use and keep track of it so the figures are handy and correct (you can do it yourself or hire a third-party—but somebody has to do this)
Baselining gets you a reference for future energy use. You use the baseline both to compare versus future performance and to compare performance to performance of a set of peer buildings.
Analysis and Evaluation—we start with simple tables and graphs for analysis. Evaluation means you have to figure out the impact of your changes: how much difference in energy use is associated with your changes?

## Slide 56: What About Energy Audits?
ENERGY STAR: audits in the analysis and
We recommend other work FIRST!
Stay tuned: audits defined and discussed later…
Assessing Performance and Setting Goals
Notes: ENERGY STAR includes audits as part of its Analysis and Evaluation sub-step—which makes sense if you are focused on capital improvements.
ASHRAE defines Preliminary Energy Analysis and three Levels of Audit.
We’ll cover ingredients of Preliminary Energy Analysis now—getting your utility information organized and evaluated.
We’ll discuss formal audits at the end of the ASSESS PERFORMANCE step in the ENERGY STAR flowchart.
Why do we defer audits until later in the course?
Because there is other work to do first, so you can take advantage of an audit. We recommend that you begin with what you can do now—getting a basic understanding of energy data relevant to the buildings you manage will give you the basis to go deeper with energy audits (to specify what you want your consultants to provide AND to use the information they provide you.)

## Slide 57
57
ANSI/ASHRAE/IESNA Standard 100-2018
Assessing Performance and Setting Goals
NEW!
Notes: Standard 100-2006 is an excellent short reference that gives practical ideas about performance measurement that complements our seminar presentation.
It is being rewritten to be even more useful.
For example here is a list of sources of energy data relevant to energy management from paragraph 5.4
Building Energy Use and Electrical Demand Data
Invoices from utilities and fuel suppliers
Detailed printouts from time-of-use meters
Combustion efficiency, eddy current and water quality tests
Recording of temperature and relative humidity
Interviews with building owners, managers and operators
Sub-metered data
Data from building pressurization/depressurization
Event recording
Climatic recordings
Sets of data from similar buildings in similar climates
Computer modeling
Production records
Infrared scans
The standard summarizes information from other AHSRAE publications, for example Energy Audits.
Many sources of information…where should you start?
We will give you some examples of metering data from the utility, from local metering and stand-alone data loggers.
Building control systems can also provide trend logs of temperatures and tables of set points useful to your work.
Seminar participants can receive a discount on ASHRAE Standard 100-2006, Energy Conservation in Existing Buildings, please contact Kim Gates at kgates@ashrae.org
You can order this standard and other ASHRAE publications through the on-line ASHRAE bookstore.
57

## Slide 58
58
ANSI/ASHRAE/IESNA Standard 100-2018
Energy Efficiency in Existing Buildings
Assessing Performance and Setting Goals
Excerpts from Table of Contents:
  Compliance
  Energy Management Plan
  O&M Requirements
  Energy Audit Requirements
  Implementation and Verification
  Energy Efficiency Measures
  Payback and Life-Cycle Cost Analysis
  Building Energy Modeling
Notes: Standard 100-2006 is an excellent short reference that gives practical ideas about performance measurement that complements our seminar presentation.
It is being rewritten to be even more useful.
For example here is a list of sources of energy data relevant to energy management from paragraph 5.4
Building Energy Use and Electrical Demand Data
Invoices from utilities and fuel suppliers
Detailed printouts from time-of-use meters
Combustion efficiency, eddy current and water quality tests
Recording of temperature and relative humidity
Interviews with building owners, managers and operators
Sub-metered data
Data from building pressurization/depressurization
Event recording
Climatic recordings
Sets of data from similar buildings in similar climates
Computer modeling
Production records
Infrared scans
The standard summarizes information from other AHSRAE publications, for example Energy Audits.
Many sources of information…where should you start?
We will give you some examples of metering data from the utility, from local metering and stand-alone data loggers.
Building control systems can also provide trend logs of temperatures and tables of set points useful to your work.
Seminar participants can receive a discount on ASHRAE Standard 100-2006, Energy Conservation in Existing Buildings, please contact Kim Gates at kgates@ashrae.org
You can order this standard and other ASHRAE publications through the on-line ASHRAE bookstore.
58

## Slide 59
59
Assessing Performance and Setting Goals
ASHRAE Standard 100-2018, Energy Efficiency in Existing Buildings
Energy Targets
Excerpts from Table 7-2a
Target values derived from CBECS 2003 and represent the 25th lowest percentile of energy use by each building category.
Notes: Standard 100-2006 is an excellent short reference that gives practical ideas about performance measurement that complements our seminar presentation.
It is being rewritten to be even more useful.
For example here is a list of sources of energy data relevant to energy management from paragraph 5.4
Building Energy Use and Electrical Demand Data
Invoices from utilities and fuel suppliers
Detailed printouts from time-of-use meters
Combustion efficiency, eddy current and water quality tests
Recording of temperature and relative humidity
Interviews with building owners, managers and operators
Sub-metered data
Data from building pressurization/depressurization
Event recording
Climatic recordings
Sets of data from similar buildings in similar climates
Computer modeling
Production records
Infrared scans
The standard summarizes information from other AHSRAE publications, for example Energy Audits.
Many sources of information…where should you start?
We will give you some examples of metering data from the utility, from local metering and stand-alone data loggers.
Building control systems can also provide trend logs of temperatures and tables of set points useful to your work.
Seminar participants can receive a discount on ASHRAE Standard 100-2006, Energy Conservation in Existing Buildings, please contact Kim Gates at kgates@ashrae.org
You can order this standard and other ASHRAE publications through the on-line ASHRAE bookstore.
59

## Slide 60
60
Assessing Performance and Setting Goals
ASHRAE Standard 100-2018: Climate Zones Map

## Slide 61
61
Assessing Performance and Setting Goals
ASHRAE Standard 100-2018, Energy Efficiency in Existing Buildings
Operating Shifts
Excerpts from Table 7-3
Notes: Standard 100-2006 is an excellent short reference that gives practical ideas about performance measurement that complements our seminar presentation.
It is being rewritten to be even more useful.
For example here is a list of sources of energy data relevant to energy management from paragraph 5.4
Building Energy Use and Electrical Demand Data
Invoices from utilities and fuel suppliers
Detailed printouts from time-of-use meters
Combustion efficiency, eddy current and water quality tests
Recording of temperature and relative humidity
Interviews with building owners, managers and operators
Sub-metered data
Data from building pressurization/depressurization
Event recording
Climatic recordings
Sets of data from similar buildings in similar climates
Computer modeling
Production records
Infrared scans
The standard summarizes information from other AHSRAE publications, for example Energy Audits.
Many sources of information…where should you start?
We will give you some examples of metering data from the utility, from local metering and stand-alone data loggers.
Building control systems can also provide trend logs of temperatures and tables of set points useful to your work.
Seminar participants can receive a discount on ASHRAE Standard 100-2006, Energy Conservation in Existing Buildings, please contact Kim Gates at kgates@ashrae.org
You can order this standard and other ASHRAE publications through the on-line ASHRAE bookstore.
61

## Slide 62
Assess Performance:
Year, Month, and Daily Data
Annual usage
  Energy cost index (ECI)
  Energy utilization index (EUI)
Annual profile of monthly data
Daily profile of 15-minute data
Assessing Performance and Setting Goals
Notes: Let’s start with analysis of one building. We’ll address working with a portfolio of buildings a little later.
We want to approach this in a systematic way.
We will work our way down to finer time scale—working from YEAR to MONTH to DAILY scales.
At each level of assessment, you want to look for data clues that will focus your attention on buildings and energy systems ripe for improvement.
If you see unusual patterns in the performance data, you need to relate the patterns to the physical systems and settings in your buildings. Your approach to the task should be like a detective, looking for clues in the data and relating the clues to energy wasting “suspects.”
We’ll start with annual usage and define some terms.

## Slide 63
Indices
ECI: Energy Cost Index = $/SF/yr
EUI: Energy Utilization Index = kBtu/SF/yr
(Annual kWh × 3.413) =_____kBtu
+ (Annual Therms × 100) =_____kBtu
Total Annual Energy =_____kBtu
EUI = Total Annual Energy ÷ SF = kBtu/SF/yr
Example: Lowell Hall @ UW
(1,209,319 kWh × 3.413) = 4,127,000 kBtu
+ (83,642 Therms × 100) = 8,364,200 kBtu
Total Annual Energy = 12,491,200 kBtu
EUI = 12,491,200 kBtu ÷ 117,600 SF = 106.2 kBtu/SF/yr
Assessing Performance and Setting Goals
Notes: Let’s begin with the basic terms.
The Energy Cost Index and Energy Utilization Index are two starting points. As the definitions show, the scaling is by the area of the building and we look at 12 months of data to capture seasonal swings in energy use.
ECI is easy to understand.
EUI takes the energy use of a building typically gas and electricity, sometimes coal, oil or steam—puts on a common basis of BTUS of energy.
We have a simple example here of a building that uses electric and gas energy, there are conversion factors for each type of energy.
EUI typically ranges from below 50 for an efficient office building to 400 or 500 for an inefficient hospital.
BACKGROUND
What’s a BTU?
In energy work outside the research setting in the U.S., almost everyone uses common units– based on pounds, degrees F, cubic feet (of gas) and British Thermal Units (Btu’s). (If you prefer to work in SI units like kilograms, degrees C or K, and joules, just recognize that you will have to use customary units much of the time when working with utility bills and energy conservation in the U.S.)
A British Thermal Unit (Btu) is defined as the energy needed to raise one pound of water one degree F at standard temperature and pressure conditions. kBtu is one thousand Btu’s.
Electric energy is commonly measured in kilowatt-hours (kWh) or a multiple (e.g. megawatt-hours); natural gas energy is commonly measured in therms or a multiple (e.g. decatherm).
The conversion factor from kWh to kBtu is 3.413; the conversion factor from therms to kBtu is 100.

## Slide 64: Energy Intensity of Office Buildings and ENERGY STAR Score
100
1
25
50
75
Energy Performance Rating
Energy Use
Highest
Lowest
Assessing Performance and Setting Goals
29.9
339.4
165.1
121.1
86.0
EUI for Office Buildings (kBtu/ft²·year)
Normalized EUI varies widely
Age and equipment not significant drivers of EUI
The ENERGY STAR rating system overlays a 1 to 100 scale over national data, giving relative meaning to energy use
Number of Buildings
Median
Notes: Just as EPA developed ways by which we measure the fuel efficiency of cars, EPA also developed a way to measure the energy efficiency of buildings. It is called the national energy performance rating system.
This is the FLIP of the schematic we discussed before the last exercise. Note that the LOWEST energy performers are on the RIGHT of this schematic, with a score of 100. The HIGHEST energy performers on the LEFT of this schematic with a score of 1.
The Energy Performance Rating System is based on data from the U.S. commercial buildings energy consumption survey (CBECS) conducted by EIA/DOE. The rating system developed by EPA overlays a 1 to 100 scale over this national data set, which gives relative meaning to energy use.
Based on the information about your customer’s facility -- such as its size, location, number of occupants, number of PCs, operating hours -- the rating system estimates how much energy the facility would use if it were the best performing, the worst performing, and every level in between. The system then compares the actual energy data entered to the estimate to determine where the facility ranks relative to its peers. On the rating system scale, 50 is the industry average, the top performers will be closer to 100, while the low performers will be closer to 1.
ES score of 75 is what many people aspire to achieve—if you can score 75 or above on the database, you can receive a plaque and recognition.
There is another level in the system, with a score of 40, if you can raise your SCORE by 10 points (not 10%),you can be recognized by Energy Star as a leader.
Slide courtesy of ENERGY STAR prepared for ASHRAE educational purposes.

## Slide 65: Exercise 2: EUI and ECI Questions
Assessing Performance and Setting Goals
Page 6
in the exercises
Notes: Turn to Page 6. Take a few minutes to read the description and answer the questions.
ANSWERS :
1 b.
2 c.
3 answer depends on the assumptions you make.
How many say a?
How many say b?
How many say c?
Ask people to explain their choices.
If you assume energy end uses and equipment and utllity charges are the ”same as Doty” in the new pub then you can pick a.
If you assume energy end uses and equipment are the “same as Doty” you can pick b.
If you assume nothing, then choose c.

## Slide 66
BREAK!

## Slide 67
Benchmarking Using
ENERGY STAR’s
Portfolio Manager www.energystar.gov/benchmark
https://www.energystar.gov/buildings/training/slide_library
Assessing Performance and Setting Goals
Notes: The ENERGY STAR benchmarking is a service FREE to users—you just need to enter information into tables, after getting an account.
The benchmarking provides a standardized, comparable metric of whole building energy performance
Traditionally there have been barriers to understanding a facility’s energy performance.
There has not been a way to compare performance between facilities
There has not been a way to measure results in a meaningful standardized approach
There has not been a means for unbiased third party verification
ENERGY STAR Benchmarking aims to remove these barriers.
The ENERGY STAR website is HUGE, so we recommend you get to the BENCHMARK section directly to cut through information about refirgerators and light bulbs.

## Slide 68
Worship
Facilities
Medical Offices
Office Buildings
Hospitals
Non-refrigerated Warehouses
Distribution Center
Supermarkets
Courthouses
K-12 Schools
Hotels
Wastewater Treatment Plants
Retail Stores
ENERGY STAR Score Eligible Building Types
Data Centers
Barracks
Bank Branches
Financial Offices
Multifamily
Housing
Refrigerated
Warehouses
Residence Hall
Wholesale Club/ Supercenter
Senior Care Community
Notes: The 1 to 100 energy performance rating is available for all the space types shown on this slide.
Additionally, for all buildings, Portfolio Manager also provides a weather normalized EUI and Greenhouse Gas Emissions calculated by the EPA. This is valuable data that you can make available for all your customers regardless of their buildings type. For instance if you have a library or a restaurant, the building can’t receive a 1 to 100 rating but inputting the building online or submitting it through automated benchmarking allows you to receive a weather normalized energy intensity value and the GHG emissions for CO2, methane, and nitrous oxide.
Slide courtesy of ENERGY STAR prepared for ASHRAE educational purposes.
68

## Slide 69: Obtaining an Energy Performance Rating
ENERGY STAR Portfolio Manager—Existing Commercial Buildings
ENERGY STAR Target Finder—Commercial New Construction Projects
www.energystar.gov/targetfinder.
www.energystar.gov/benchmark.
Assessing Performance and Setting Goals
Notes: This 1-100 energy performance rating can be accessed in 2 ways:
Existing commercial buildings can use ENERGY STAR Portfolio Manager.
Data needed includes:
Location (address, zip code)
Energy consumption data (most recent 12 consecutive months of utility bills for all major sources of energy, including electricity, gas, oil, and/or steam for the same 12 month period)
Space Type information specific to the activity taking place in the facility (SF, # of rooms, etc.)
New construction projects can use ENERGY STAR Target Finder.
Target Finder works in the same way Portfolio Manager does. The rating you receive is based on projected energy use of the building design.
Both tools are available online at no cost to all interested users.

## Slide 70
Why Benchmark?
ENERGY STAR Says:
Heighten awareness of energy use
Assess effectiveness of current operations, policies, practices
Set priorities for upgrade efforts and retrofits
Track, verify, and recognize achievements
Document role in environmental stewardship and demonstrate success
Assessing Performance and Setting Goals
Notes: 70
Slide courtesy of ENERGY STAR prepared for ASHRAE educational purposes.

## Slide 71: Benchmarking with Portfolio Manager
Compare buildings against similar buildings nationwide and against other buildings in your portfolio
Receive an ENERGY STAR score normalized for weather
Identify opportunities and set priorities for upgrade investments
Track and manage:
  Energy consumption and costs over time
  Direct, indirect, and total greenhouse gas emissions
Gain recognition from EPA for success!
Assessing Performance and Setting Goals
Notes: Benchmarking in Portfolio Manager helps you organize a portfolio of buildings, with special benefit to the normalized energy use and ability to compare your buildings to similar buildings. (Review slide.)
RECOGNITION from EPA is “icing on the cake”—the fundamental use of the rating system is to provide you with information to improve use of energy in your buildings.
Slide courtesy of ENERGY STAR prepared for ASHRAE educational purposes.

## Slide 72
Getting Started with
ENERGY STAR Benchmarking www.energystar.gov/benchmark
Assessing Performance and Setting Goals
Notes: It is a huge website, to get to the benchmarking section, you can cut thru information about refrigerators.

## Slide 73
73
Assessing Performance and Setting Goals

## Slide 74
74
Assessing Performance and Setting Goals

## Slide 75
75
Assessing Performance and Setting Goals

## Slide 76
76
Assessing Performance and Setting Goals

## Slide 77: Track Facility Energy Performance
Assessing Performance and Setting Goals
Notes: Once all space and energy data information has been inputted for a property, Portfolio Manager will generate an energy performance rating for facilities that meet the eligibility requirements for receiving a rating.
Notice that currently the “Summary: Energy Use” View is selected for this sample facility, which scores a 73 on he energy performance rating scale. Portfolio Manager users can choose from several pre-populated “Views” (shown in the drop down menu on this slide) or create their own customized view, by clicking “Create View”. There are approximately 50 data columns to choose from to allow you to display the exact information you need to provide a snapshot of progress at a customer’s request.
LIMITATION OF PORTFOLIO MANAGER: There is no way at present to track peak demand (kW) for electric meters. Peak demand is a large component of most commercial bills and cost effective actions can aim at reducing peak demand, either by shifting use or by absolute energy reduction during peak periods.
Slide courtesy of ENERGY STAR prepared for ASHRAE educational purposes.

## Slide 78: Greenhouse Gas Emissions
Assessing Performance and Setting Goals
Notes: Here’s a screenshot of the “GHG Emissions View” in Portfolio Manager, which provides a summary of emissions of a building (direct, indirect, change from baseline measures). You can use this to report and help building owners and managers track their emissions.
The GHG emissions are based on the location of the building within the 27 subregions of the U.S. power grid. These sub-regions are defined by EPA’s Emissions and Generation Resource Integrated Database (eGRID).
In the example, The SERC Virginia/Carolina region represents a section of the power grid with similar emissions and resource mix characteristics.
Here’s a link to a map of the regions: https://www.energystar.gov/istar/pmpam/help/eGrid_Subregion_Map.htm
In the example, the estimated emissions of CO2e (in kg per MBtu) is 151.7 or 0.1517 Metric tons per MBtu.
The table shows 612.9078 Mbtu (converting kBtu to MBtu, divide by 1,000)
151.7 x 612.9078 gives 92.98 MtCO2e (difference due to number of signficant digits and rounding in the emissions calculator)
NOTE: the little “e” next to the CO2 indicates that Portfolio Manager has converted two other greenhouse gases, methane (CH4) and nitrous oxide (N2O) into the emissions equivalent of CO2. In the technical document from ENERGY STAR “Greenhouse Gas Inventory and Tracking in Portfolio Manager” (8/31/2009), it states “CO2 represents more than 99% of the total greenhouse gas emissions from fuels combusted by commercial, industrial and electricity production sources” so as a good approximation, the emissionsy ou see in Portfolio Manager are CO2 emissions
Slide courtesy of ENERGY STAR prepared for ASHRAE educational purposes; amended for today’s seminar.

## Slide 79: Portfolio Manager Metrics Comparison
Assessing Performance and Setting Goals
Notes: Here’s a screenshot of the “GHG Emissions View” in Portfolio Manager, which provides a summary of emissions of a building (direct, indirect, change from baseline measures). You can use this to report and help building owners and managers track their emissions.
The GHG emissions are based on the location of the building within the 27 subregions of the U.S. power grid. These sub-regions are defined by EPA’s Emissions and Generation Resource Integrated Database (eGRID).
In the example, The SERC Virginia/Carolina region represents a section of the power grid with similar emissions and resource mix characteristics.
Here’s a link to a map of the regions: https://www.energystar.gov/istar/pmpam/help/eGrid_Subregion_Map.htm
In the example, the estimated emissions of CO2e (in kg per MBtu) is 151.7 or 0.1517 Metric tons per MBtu.
The table shows 612.9078 Mbtu (converting kBtu to MBtu, divide by 1,000)
151.7 x 612.9078 gives 92.98 MtCO2e (difference due to number of signficant digits and rounding in the emissions calculator)
NOTE: the little “e” next to the CO2 indicates that Portfolio Manager has converted two other greenhouse gases, methane (CH4) and nitrous oxide (N2O) into the emissions equivalent of CO2. In the technical document from ENERGY STAR “Greenhouse Gas Inventory and Tracking in Portfolio Manager” (8/31/2009), it states “CO2 represents more than 99% of the total greenhouse gas emissions from fuels combusted by commercial, industrial and electricity production sources” so as a good approximation, the emissionsy ou see in Portfolio Manager are CO2 emissions
Slide courtesy of ENERGY STAR prepared for ASHRAE educational purposes; amended for today’s seminar.

## Slide 80: Statement of Energy Performance
Assessing Performance and Setting Goals
2013
2018
Notes: The Statement of Energy Performance (SEP) can be generated in Portfolio Manager for each building. It is a summary of energy and environmental performance for a building. The SEP is required to apply for the ENERGY STAR label.
Also, the SEP can also be used as a transactional document (e.g. especially for CRE—Commercial Real Estate) to communicate building performance to potential tenants, buyers, etc.
Note added 9 October 2009: Portfolio Manager announced enhanced reporting capabilities 10/9/2009. Additional features have been added to the basic information we show.

## Slide 81
Assessing Performance and Setting Goals
Changes to Waukesha Memorial Hospital Since 2013
Upgraded controls on AHUs
  Reset duct pressure setpoint
  Reset supply air temperature
  Economizer at 62°F
  Optimal start
Replace AHUs
  New fans with VFDs
  Hot water instead of steam heat
  Chilled water instead of DX cooling
New chiller plant
  Magnetic bearing centrifugal chillers
  Cooling towers with VFDs and indoor sump
Replace constant-volume reheat with VAV with reheat
Notes: The Statement of Energy Performance (SEP) can be generated in Portfolio Manager for each building. It is a summary of energy and environmental performance for a building. The SEP is required to apply for the ENERGY STAR label.
Also, the SEP can also be used as a transactional document (e.g. especially for CRE—Commercial Real Estate) to communicate building performance to potential tenants, buyers, etc.
Note added 9 October 2009: Portfolio Manager announced enhanced reporting capabilities 10/9/2009. Additional features have been added to the basic information we show.

## Slide 82: Track Portfolio Energy Performance
Assessing Performance and Setting Goals
Notes: In addition to tracking and managing energy use of customer’s single buildings, Portfolio Manager also allows you to help customers track performance across multiple buildings or an entire portfolio of buildings.

## Slide 83: How Do I Enter a Facility that is Not Located in the United States?
“You may create a facility that is not located in the United States in the same way that you create other facilities: select ‘Add Facility’ from the My Portfolio page in Portfolio Manager and enter the required information. After you select the Country, you will be asked to select the city outside of the United States that is closest to your facility from a dropdown list.”
—ENERGY STAR Website

## Slide 84: Can a Building Located Outside of the United States Earn the ENERGY STAR?
“The only buildings located outside of the U.S. that are eligible to earn the ENERGY STAR are those that are owned and occupied by the U.S. Government and that have met U.S. construction codes.”
- ENERGY STAR Website

## Slide 85: All Buildings Can Benchmark, but Some Cannot Receive a Rating
Benchmark your facility against itself
  Look at trends in historical data
Compare to other buildings in your portfolio
  Prioritize upgrade opportunities
  Create an internal benchmark
  “Create a Group” to compare select buildings
Compare to national average energy use intensity (EUI) or ASHRAE Standard 100-2018 for your building type
  Set performance targets
Assessing Performance and Setting Goals
Notes: As mentioned previously, if a space type is not eligible to receive an energy performance rating at this time, it should still benchmark in Portfolio Manager! It can still… (review slide).
Also, if the building is not eligible for a rating, you will not be able to generate a Statement of Energy Performance, which uses the rating as a fundamental ingredient.
Slide courtesy of ENERGY STAR prepared for ASHRAE educational purposes.

## Slide 86: Ways to Obtain the Rating or EUI
Single Building Manual Entry
  Enter building and energy consumption information into Portfolio Manager
Excel Data Upload
  Upload building data in Portfolio Manager using an Excel template
Automated Benchmarking Services
  Use an ENERGY STAR service and product provider to have the rating automatically integrated into your energy information and bill handling system for all buildings
Assessing Performance and Setting Goals
Notes: 86
There are 3 main ways to enter the information required by Portfolio Manager and obtain an energy performance rating for your customers:
1. Go online to ENERGY STAR Web site (www.energystar.gov/benchmark) and login to the tool and create an account and begin entering data for each customer building;
2. Take advantage of excel data templates for bulk data uploads of 10 or more new properties of the same building type (e.g. 10 office buildings, 10 retail stores);
3. Offer automated benchmarking services or work with another ENERGY STAR Service and Product Provider who offers automated benchmarking services. Automated benchmarking is a way to have the rating automatically integrated into energy information and bill handling reports through software offered by the SPP. This lets customers receive monthly ratings in the same Web-based or reporting interface that you/your customer may already use to communicate other energy and building information.

## Slide 87: Information Required for Rating
K-12
School
SF*
Office
Hospitals
% heated
All
Space Types
Address
# Walk-in refrigerator/ freezer units
# PCs
Open weekends: Y/N
Cooking: Y/N
High school: Y/N
SF*
Op. hrs.
# Workers
SF*
# workers
# MRI machines
# floors
# PCs
% heated
% AC
Year Built
At least 12 months energy data
% heated
% AC
% AC
Licensed and staffed bed capacity
Laundry
Tertiary care
Laboratory
Examples
87
Assessing Performance and Setting Goals
*Gross square feet—deduct “upper floors” of atria
Notes: The ENERGY STAR Benchmarking Starter Kit includes a Data Collection Worksheet, which can be used to facilitate the data collection process. Benchmarking Starter Kit Web page: http://www.energystar.gov/index.cfm?c=evaluate_performance.bus_portfoliomanager_benchmarking
For all space types, the following information is needed:
The facility’s address, the year it was built, and at least 12 months of energy data.
The energy consumption data is collected by gathering the most recent 12 consecutive months of utility bills—you will need data for all major sources of energy. For example, if your facility uses electricity, natural gas, and oil, you need to collect energy data for all of these energy sources for the same 12 months. (Note: you can enter data going back even further to see changes over time.)
The required space data will depend on the space type.
This slide shows the required space data for three examples: K-12 Schools, Office buildings and supermarket/grocery stores.
Slide courtesy of ENERGY STAR prepared for ASHRAE educational purposes.
Note added about Hospitals: Required information includes
SF
# of beds
# of floors
Tertiary care Y/N

## Slide 88: ENERGY STAR Rating as a Quick Guide
If your building has a low score (less than 25), there are likely to be many opportunities.
If your building has a high score (more than 75):
  Confirm that you can monitor to keep it there
  Go look for another building to improve
Assessing Performance and Setting Goals
Notes: The ENERGY STAR benchmark provides an EXTERNAL benchmark. If you have multiple facilities, you can benchmark within your organization—comparing performance to guide your next steps.

## Slide 89: Track Water Use Too
Assessing Performance and Setting Goals
Notes: Portfolio Manager also allows you to track water use by building. You define meters and track utility units in the same way as for energy meters. PM allows you to record water bills annually or for six month periods if your water billing is not on a monthly basis.

## Slide 90: ENERGY STAR “75+” Recognition
- Listed on the website
- Wall plaque
- Citation from EPA
Assessing Performance and Setting Goals
Notes: For official recognition, the information submitted to ENERGY STAR for rating must be verified by a Professional Engineer.
The building must also comply with performance standards for Indoor Environmental Conditions:
Ventilation for Acceptable Indoor Air Quality (ASHRAE Standard 62)
Acceptable Thermal Environmental Conditions (ASHRAE Standard 55)
Adequate Illumination (IESNA Lighting Handbook)
Buildings with ratings that show a 10 point increase over baseline can receive a Recognition Certificate for any scores (not just >=75).
Facility locator shown on the slide is found at
https://www.energystar.gov/index.cfm?fuseaction=labeled_buildings.locator

## Slide 91
For more information on
ENERGY STAR Benchmarking visit:
https://www.energystar.gov/
buildings/training/slide_library
Assessing Performance and Setting Goals
Notes: It is a huge website, to get to the benchmarking section, you can cut thru information about refrigerators.

## Slide 92: Exercise 3: Portfolio Manager Facility Report
Assessing Performance and Setting Goals
Page 8
in the exercises
Notes: Turn to page 8 in the Exercises.
Answers:
Choice iv A, C, D are correct.
Choice iii B, C, D are correct. (for statement B, it is easier to use the scaled GHG emissions than the total tons!)
Any additional Questions?

## Slide 93: Site Versus Source Energy
222 = 66 × 3.340
Assessing Performance and Setting Goals
Notes: The ENERGY STAR Rating system uses source energy to put energy use by buildings on a common basis, accounting for fuel mix differences among buildings. For example, electric resistance heating can appear more efficient than other forms of heating if only site use is considered—but when you factor in the energy needed to generate the electricity, electric resistance heating is much less efficient than typical heating by natural gas.
Portfolio Manager uses a set of factors to transform site energy into source energy units. In the slide, we show the arithmetic to convert site annualized Energy Intensity of 66 kBtu/sq ft/yr into source annualized Energy Intensity: multiply 66 by the factor 3.340 to get 222 kBtu/sq ft/yr.
“Most building managers are familiar with site energy, the amount of heat and electricity consumed by a building as reflected in utility bills. Site energy may be delivered to a facility in one of two forms: primary and/or secondary energy. Primary energy is the raw fuel that is burned to create heat and electricity, such as natural gas or fuel oil used in onsite generation. Secondary energy is the energy product (heat or electricity) created from a raw fuel, such as electricity purchased from the grid or heat received from a district steam system. A unit of primary and a unit of secondary energy consumed at the site are not directly comparable because one represents a raw fuel while the other represents a converted fuel. Therefore, in order to assess the relative efficiencies of buildings with varying proportions of primary and secondary energy consumption, it is necessary to convert these two types of energy into equivalent units of raw fuel consumed to generate that one unit of energy consumed on-site. To achieve this equivalency, EPA uses the convention of source energy.”
(p. 1, Methodology for Incorporating Source Energy Use: http://www.energystar.gov/ia/business/evaluate_performance/site_source.pdf)

## Slide 94: Practical Implications
Don’t mix site and source energy values in your analysis
Not all source energy calculations use the EPA method
Site energy drives basic $ costs
Source energy drives environmental costs
Assessing Performance and Setting Goals
Notes: If you are discussing EUI of your buildings, it is easy to mix up site and source versions. If an EUI is not labeled, it is likely to be based on site energy.
Porftolio Manager documents use clear labels and headings to distinguish site and source energy calculated using the EPA national method.
Calculations of source energy can use regional or local measures—not all source energy numbers are computed the same way. U.S. government documents typically describe the methods to calculate the numbers in footnotes and references.
Your dollar costs will be based on site energy.
When costs of carbon are incorporated into utility bills, these will account for source energy, perhaps on a regional basis (reflecting the generation mix in each region.)
The emissions estimated by Portfolio Manager are derived from regional estimates. Regions like the upper MidWest use a lot of coal for generation and have a higher carbon burden than regions like the Pacific Northwest, which have a lot of hydroelectric generation.

## Slide 95: Reference Schematic of EPA Tools on ENERGY STAR Site
3. Understand financial value
1. Commit to energy efficiency
6. Communicate results
2. Identify
qualified projects
5. Demonstrate results
4. Implement quality projects and evaluate
EPA Tools Support the Energy Management Process
Assessing Performance and Setting Goals
Notes: As you can see, ENERGY STAR’s offerings directly support your current process and needs. Building owners/managers and SPPs can easily incorporate ENERGY STAR’s tools and resources to advance energy management efforts (Buildings), or add value to your current offerings (SPPs).
Building owners can locate expert help through the ENERGY STAR Partnership (and SPPs can find identify prospects) by connecting with other ENERGY STAR Partners. Identify potential projects using the Energy Performance rating Tools provided by ENERGY STAR, move proposals to contract using the many financial tools and resources to help communicate the financial value of upgrade projects, implement projects and evaluate them using guides and resources provided by ENERGY STAR to help establish goals and develop strategies , demonstrate results using the Energy Performance Rating tool again and gain recognition through ENERGY STAR to help communicate those results by qualifying for the label or some other milestone.
This slide was prepared by ENERGY STAR and used with their permission.

## Slide 96: Reference Schematic of EPA Tools on ENERGY STAR Site
3. Understand financial value
Financial Tools
1. Commit to energy efficiency
ENERGY STAR
Partnership
6. Communicate results
Recognition, Results, Label
2. Identify
qualified projects
Energy Performance Rating Tools
5. Demonstrate results
Energy Performance Rating Tools
4. Implement quality projects and evaluate
Technical
Resources
EPA Tools Support the Energy Management Process
Assessing Performance and Setting Goals
Notes: As you can see, ENERGY STAR’s offerings directly support your current process and needs. Building owners/managers and SPPs can easily incorporate ENERGY STAR’s tools and resources to advance energy management efforts (Buildings), or add value to your current offerings (SPPs).
Building owners can locate expert help through the ENERGY STAR Partnership (and SPPs can find identify prospects) by connecting with other ENERGY STAR Partners. Identify potential projects using the Energy Performance rating Tools provided by ENERGY STAR, move proposals to contract using the many financial tools and resources to help communicate the financial value of upgrade projects, implement projects and evaluate them using guides and resources provided by ENERGY STAR to help establish goals and develop strategies , demonstrate results using the Energy Performance Rating tool again and gain recognition through ENERGY STAR to help communicate those results by qualifying for the label or some other milestone.
This slide was prepared by ENERGY STAR and used with their permission.

## Slide 97
Assess Performance
Annual usage
  Energy cost index (ECI)
  Energy utilization index (EUI)
Annual profile of monthly data
Daily profile of 15-minute data
Assessing Performance and Setting Goals
Notes: Now back to our topic “Assess Performance”.
Moving beyond the starting point of Annual Usage, let’s begin to look at profiles of monthly data and using Monthly Data to find opportunities for improvement.
A picture is worth a thousand words or entries in a table—what does a GRAPH of your monthly data tell you?

## Slide 98
Madison Church
Annual Profile of Monthly Data
Chart: Gas
| 36892 | 36923 | 36951 | 36982 | 37012 | 37043 | 37073 | 37104 | 37135 | 37165 | 37196 | 37226
2001 | 4652 | 3479 | 3733 | 3382 | 1521 | 59 | 76 | 22 | 42 | 74 | 1989 | 2230
2012 | 3580 | 2478 | 1338 | 756 | 60 | 69 | 66 | 77 | 870 | 1945 | 2709 | 3774
Assessing Performance and Setting Goals

## Slide 99
Madison Church
Annual Profile of Monthly Data
Chart: Electric
| 36892 | 36923 | 36951 | 36982 | 37012 | 37043 | 37073 | 37104 | 37135 | 37165 | 37196 | 37226
2001 | 13440 | 10320 | 12080 | 10320 | 9520 | 7440 | 6880 | 9840 | 9440 | 8560 | 8480 | 9840
Predicted | 9000 | 9000 | 9000 | 9000 | 10000 | 11000 | 11750 | 12000 | 11500 | 10500 | 9500 | 9000
Assessing Performance and Setting Goals

## Slide 100
Madison Church
Annual Profile of Monthly Data
Chart: Electric
| 36892 | 36923 | 36951 | 36982 | 37012 | 37043 | 37073 | 37104 | 37135 | 37165 | 37196 | 37226
2001 | 13440 | 10320 | 12080 | 10320 | 9520 | 7440 | 6880 | 9840 | 9440 | 8560 | 8480 | 9840
2011 | 13434 | 12643 | 11310 | 10654 | 9228 | 12810 | 12006 | 11126 | 10919 | 10749 | 11944 | 13385
2012 | 12261 | 12824 | 11767 | 9955 | 12097 | 15488 | 15073 | 14624 | 12058 | 11616 | 11712 | 12513
Predicted | 9000 | 9000 | 9000 | 9000 | 10000 | 11000 | 11750 | 12000 | 11500 | 10500 | 9500 | 9000
Assessing Performance and Setting Goals

## Slide 101: Exercises 4A and 4B: Monthly Electric and Gas Profiles
Assessing Performance and Setting Goals
Page 11
in the exercises
Notes: Turn to p 11 for Exercise 4A (electricity) and then to p. 13 for 4B (gas).
4A Answer: b) Statements 1, 2 and 4 are supported by the graphs. It looks like in 2008, Doty Street is using less electric energy than in the previous two years.
Any questions? (Instructor may point out the discussion of peak demand).
4B Answer: d) Statements 2, 3 and 4 are supported by the graphs. Statement 1 is not supported (except for March 2006, the HDD graph has the same shapes as the Therms/Day graph shapes.
(typo at the top of page 14: Sentence about Therms per day “to help us understand base USE…”
Any questions? (Instructor may point out the discussion of HDD and the reference temperature choice).

## Slide 102
102
Assess Performance
Annual usage
  Energy cost index (ECI)
  Energy utilization index (EUI)
Annual profile of monthly data
Daily profile of 15-minute data
Assessing Performance and Setting Goals
Notes: Now we will look at daily data (mostly electricity energy use) in 15-minute increments or intervals. This kind of data is thus called interval data.
You can learn a lot more from interval data than from annual or monthly data.
15-minute electricity data are common in energy management applications for two reasons:
Many utilities charge peak average demand using 15-minute intervals (the utility will look at the peak 15 minute period over the billing cycle or over the past 12 months and then add a surcharge for this peak use. Using the analogy of a car dashboard, demand is like your speedometer, it is the rate at which you are using energy; energy itself is like the odometer, tracking amount of energy used.).
For many HVAC and lighting applications for entire buildings or major sections of buildings, you can see the patterns of use and changes with an observation every 15 minutes. Looking more frequently won’t reveal more clues. This is NOT the case for detailed study of motor circuits, where you may need to be checking performance every minute (or less) to be sure to catch important clues.
102

## Slide 103
Honolulu Office Building: Using 15-Minute Data to Identify Opportunities
Assessing Performance and Setting Goals
Notes: We’ll take a look at 15-minute data for this office building in Honolulu, Hawaii.
Interval data either in 15-minute, 30-minute or hourly steps is often available for most buildings of a certain size. Check with your utility. They may be able to provide you with the data, typically in a table, looking back in time.
Some utilities provide the detailed data on a website, either free or for a modest charge. Call your utility to find out!

## Slide 104
Daily Profile of 15-Minute Data
Assessing Performance and Setting Goals
All AHUs + 1 chiller
2nd chiller
Chillers unloading
People + lights
Fully occupied
People leaving
Timer off
Building empty
Aug. 6
Notes: In Honolulu, the utility provide the graph, which is more useful than a just a table of numbers.
This is a daily profile, one day in the life of the building in Honolulu. You see the energy use rises early at 1:30 and then steps up again at 3 am.
When studying the building, one chiller, AHU and fans came on at 1:30. At 3:00, the next chiller (with AHU and fans) turns on.
Dip at 6 am comes when the cooling system is unloading, then the building wakes up when people come in. You can see the drop off at 6 pm when offices close for the day and the building goes to unoccupied mode. The use drops down slowly to a minimum at midnight.
The peak 15-minute kW use is close to 1000 at mid-day, the building demand at minimum is 200 kW.
What can you learn from this graph?
A/C is turned on way too early
stuff is not really turned off .
You can begin to go to work to reduced wasted energy, based on what you have learned.

## Slide 105
Simplified Profile
Assessing Performance and Setting Goals
kW
Notes: Here, we have colored to graph to match what we learned in the previous slide.
Red is wasted energy under our control, adjust clocks so that the A/C does not turn on in the middle of the night.
(2) The blue is more of a mystery-- “all stuff” is not off but there is roughly a constant demand of 200 kW no matter what time of day.

## Slide 106
Monday Versus Holiday
Assessing Performance and Setting Goals
Aug. 6
Sep. 3
Notes: The same year, we see that the time clocks were not aware of holidays. They turned everything on Labor Day, 9/3/2001.
So the green curve shows this is what the building uses with no lights and no people.
The energy advisor complimented the building manager because the advisor can now estimate the energy used by lights and office equipment. The building manager eliminated (by error ) the laborious task the energy advisor would have had to carry out to estimate electricity end use!
An unusual, unexpected pattern in the data helps you find waste that you can eliminate.
As ENERGY STAR’s advice says, assessment data can help you to
Prioritize poor performing facilities for immediate improvement. When you see a problem, you can begin corrective action immediately.
Develop a historical perspective and context for future actions and decisions. In this case, what does this problem tell you about HVAC settings for OTHER holidays and what needs to happen?
Establish reference points for measuring and rewarding good performance. If you fix the problem for Labor Day and assure proper performance on Thanksgiving, then you have a basis to reward good performance of the building engineer.

## Slide 107
New Software to Evaluate Interval Data
Assessing Performance and Setting Goals
Notes: ECAM takes tabular data and creates charts by day, occupancy, etc.

## Slide 108
New Software to Evaluate Interval Data
Assessing Performance and Setting Goals
ECAM for Excel from California Commissioning Collaborative
https://www.cacx.org/PIER/ecam/
Notes: ECAM takes tabular data and creates charts by day, occupancy, etc.

## Slide 109
Meters and Submeters
Meters by themselves do not save anything
No direct payback on the purchase of a meter
But… how can you manage it if you can’t measure it?
Assessing Performance and Setting Goals
Notes: Installing meters and sub-meters is a headache! Meters won’t save anything! Hard to get into a budget.
Nonetheless, you need metering!
Meters are absolutely critical for you to see patterns of use, to get clues, and to evaluate your progress.

## Slide 110
Measurement Technology
Costs decline, features improve
More options than ever
Creative thinking and competitive bidding can get you useful metering
Assessing Performance and Setting Goals
Notes: Instructor will elaborate on the slide points
Measurement technology is continuously improving, and becoming more affordable
There is often more than one way to develop measurements which are useful in an Energy Management program
Creative thinking and competitive bidding can produce surprising results
EXAMPLE: Two Big Ten campuses, near each other. One says sub-metering costs $12 million and so we can’t do it. The other says sub-metering costs $2 million and we did it.

## Slide 111
111
Prioritizing Multiple Buildings
Assessing Performance and Setting Goals
Notes: This map shows the Climate zones of and database at the time of the analysis (See subsequent slide for reference to updated climate zones and link to explanation of the climate zones).
An issue with the analysis that follows is that microclimates especially in California are not recognized by this level—it provides a first approximation to climate differences that drive energy use and was the climate approach used by the company in this case.
111

## Slide 112
112
Prioritizing Multiple Buildings
Assessing Performance and Setting Goals
Notes: All the buildings are illustrated in the same climate zone 4 shown in the previous map. All of the buildings are exposed to similar weather, to a first approximation.
The sites represent retail sites owned by the same company, selling the same products, using high intensity lighting for display, similar hours.
There are two types of stores, Homestores and Housewares. The Homestores are typically about 3 times the size of the Housewares but there is no obvious pattern in energy use related to the type of store –there are high and low energy users of both types.
When you sort the sites by EUI, the sites range from 40 to 193.
There are 2 stores in the database, were equipped with EMS (energy management system). They are not particularly efficient!
Installing something called an EMS and not performing Energy Management with it is a useless activity.
112

## Slide 113
113
Prioritizing Multiple Buildings
Assessing Performance and Setting Goals
Notes: Let’s set 115 as a target. There is a Housewares store with that EUI and a Homestore with a similar EUI.
If we could reduce all the higher ones to this level, what would we get?
113

## Slide 114
114
Prioritizing Multiple Buildings
Assessing Performance and Setting Goals
Notes: This is what we learned. If we could make this reduction in bills for the sites with EUI higher than 115, we would estimate these savings $0.3 million a year (assuming proportional impact.)
This is simply an arithmetic exercise, of course it is worthwhile to visit these buildings to decide exactly what to do to reduce energy use.
Since a priori you have a set of similar buildings,you should suspect that the buildings with relatively high EUI have issues that are relatively easy to find: things are left on at night or heating and cooling at the same time.
(Note: buildings in gray were left out of the cost exercise because they were close to the target building.)
114

## Slide 115: Climate Zone Map (2018)
Assessing Performance and Setting Goals
Notes: Here is the most current climate zone map, showing slight changes from the map used in the preceding example.
This map is useful if you are doing simple comparisons among buildings—as a first approximation, buildings in the same zone may be compared for performance. We will present more detailed methods to account for the impact of weather (temperature) on energy use later in the seminar.
More information about the current energy climate zone map is available at
http://resourcecenter.pnl.gov/cocoon/morf/ResourceCenter/article/1420

## Slide 116
Portfolio in Benchmark Order
1
100
50
75
25
Best investment opportunities are in lower quartiles, where there is the greatest potential for improvement
Invest
O&M improvements will yield savings and may be ENERGY STAR candidates
Tune
Reward and Learn
High scoring buildings provide lessons learned and may be ENERGY STAR candidates
Identify Priorities Across Portfolios
Assessing Performance and Setting Goals
ENERGY STAR Score
Notes: 116
As shared earlier, the rating system developed by EPA overlays a 1 to 100 scale over a national data set (CBECS), which gives relative meaning to energy use. On the rating system scale, 50 is the industry average, the top performers will be closer to 100, while the low performers will be closer to 1.
The energy performance rating provides a third party evaluation of commercial buildings. Scores can be understood at any level of an organization, and can be used to help set priorities across a portfolio of buildings (not just in one building). So, if you were to rate several building within a portfolio, you would find that scores may vary from one building to the next.
Buildings that score below 50 may be considered among the best candidates for investment opportunities and are good candidates for comprehensive/major upgrades
Buildings that score 50-75 are probably buildings where energy efficient technologies or operations and maintenance improvements may yield savings
And Buildings that score 75 or higher provide lessons learned and may be label candidates
The tool adjusts for factors like weather, hours of operation, number of occupants, and number of computers.
AT THE EXTREMES OF THE SCALE:
If your building has a low score (less than 25), there are likely to be many opportunities.
If your building has a high score (more than 75)
  Confirm that you can monitor to keep it there
  Go look for another building to improve
  Slide courtesy of ENERGY STAR prepared for ASHRAE educational purposes.

## Slide 117: Exercise 5: Site Targeting Case
Assessing Performance and Setting Goals
Page 15 in the exercises
Notes: Turn to page 19 in the Exercises.
(typo on the first statement, extra word ARE)
Answer: II Statements b and c are true. Statement a is not true, just use the definition of EUI.
Answer: IV All statements are true. (Statement b might be argued with: if sales are proportional to size, then Hilldale pays relatively more of its ales income for utilities than the other two pubs.)
Based on the energy table calculation HILLDALE is a good initial candidate.

## Slide 118
BREAK!

## Slide 119
119
Why Look at a Breakdown of Energy Use?
Assessing Performance and Setting Goals
Notes: 119

## Slide 120
120
What System Should I Tackle?
Assessing Performance and Setting Goals
Notes: This kind of pie chart, with solid estimates of energy use, is normally developed only with help on an energy audit.
Today we are NOT emphasizing energy audits but we want to discuss what you can learn from this type of breakdown.
You can use general breakdowns to prime your thinking. Just by looking, this gives you clues about where to start.
You can begin to get an action plan that aims at the high uses first.
You can also account informally for the cost and expense of replacing equipment. In this example, Chillers are shown as the third largest category. We would not recommend that you develop a plan to replace chillers because they are expensive; rather you would start with better operations of the chillers.
As is typical with many office buildings, lights and fans account for a lot of energy and they are obvious targets for improvement.
(The usual improvement advice is that it is easier to find waste in a big chunk of the energy pie than in a smaller chunk. That is, if you start with a category that is big, you have a greater chance of saving energy--this is related to the “Pareto” method to improve performance.)
120

## Slide 121
121
Honolulu Office Building Actual End Use
Assessing Performance and Setting Goals
Notes: Instructor to contrast this breakdown to the previous “generic” breakdown. In particular, this building is located in a tropical climate (Zone 1 on the 2004 Climate Zone Map) and we should expect a relatively high load from air-conditioning.
121

## Slide 122: Doty Street Pub—Inventory
Assessing Performance and Setting Goals
Notes: Instructor to discuss the breakdown for the Doty Street Pub.
Refrigeration, HVAC, and Lighting account for 75% of the electricity used at the site—refrigeration load is absent in an office building!
This breakdown for Doty Street used the analysis tool available from
http://www.focusonenergy.com/Business/Commercial-Business/CPEM/sixsteps.aspx

## Slide 123: How? Use a Spreadsheet Guide
Assessing Performance and Setting Goals
Notes: Instructor to step through the highlighted fields to get a rough estimate of energy uses.
Templates help you record electricity and gas energy use by equipment type—for example, for electricity, the tool gives you places to record power, hours of use, and efficiency or load factor. The spreadsheet calculates multiplies these values to give energy use. The spreadsheet also totals up the end use energy and compares to your 12 month energy use. The example shows how lighting energy, added up across all fixtures, gets totaled on the main page.
The totals are then put into a pie chart, if you want to use that view, too.
See http://www.focusonenergy.com/Business/Commercial-Business/CPEM/sixsteps.aspx

## Slide 124: Examples of End-Use Energy Calculations
Lighting example:
46 lamps × 52 watts/lamp × 0.95 load factor × 6516 h/yr × 0.001 kW/watt
14,807 kWh/yr
Fan example: 1.3 hp × 0.746 kWh/hp × 90% efficiency × 65% full load for fixed-speed motor × 1200 h/yr 840 kWh/yr
Assessing Performance and Setting Goals
Notes: Instructor to step through the example.
The referenced spreadsheet on the previous slide has generic guidance on load factors and motor efficiencies.
More precise estimates on major equipment may be made by measuring power using a current amp meter (to be done by qualified staff or contractor.)

## Slide 125
Et cetera!
Assessing Performance and Setting Goals
Notes: Spreadsheets on multiple tabs target different equipment uses and types.
The spreadsheet tool is discussed in Step 3
http://www.focusonenergy.com/Business/Commercial-Business/CPEM/sixsteps.aspx
And the link to the spreadsheet itself is
http://www.focusonenergy.com/files/Document_Management_System/Business_Programs/equipmentusage_spreadsheet.xls
You may also be interested in the equipment use by business type template, based on 15 year-old Federal survey data,
http://www.focusonenergy.com/files/Document_Management_System/Business_Programs/equipmentbybusnesstype_spreadsheet.xls
What is Focus on Energy? Wisconsin's statewide energy efficiency and renewable energy program.
Legislature created the program in 1999, expanded in 2005.
Helps implement projects that would not occur otherwise.
Customer eligibility based on their electric and/or natural gas utilities.
Focus on Energy works with eligible Wisconsin residents and businesses to install cost effective energy efficiency and renewable energy projects. Focus information, resources and financial incentives help to implement projects that otherwise would not be completed, or to complete projects sooner than scheduled. Its efforts help Wisconsin residents and businesses manage rising energy costs, promote in-state economic development, protect our environment and control the state's growing demand for electricity and natural gas. For more information, call 800.762.7077 or visit focusonenergy.com Focus on Energy offers .... Residential, Business and Renewable Energy Programs (Single and multifamily homes, commercial, industrial, agriculture and schools/government buildings) education, technical expertise and financial assistance

## Slide 126: Exercise 6: System Target Case
Assessing Performance and Setting Goals
Page 17
in the exercises
Notes: Turn to page 21 in the Exercises.
Answers:
Subsystems: Lighting, HVAC and Refrigeration account for more than 75% of electric energy use.
Comparing pubs using the estimated figures:
Statement a is true
Statement b is true: Doty St per sq ft is 26.4 kWh, Hilldale is 50.0 kWh.
Statement c is NOT TRUE, on an absolute basis, Hilldall costs less than the other two pubs.
Statement d is true.
So Choice 2 is correct.
Statement is TRUE.

## Slide 127
An Introduction to
Energy Audits:
The foundation for
smart capital investment
and
a source of O&M ideas
Assessing Performance and Setting Goals
Notes: In this section, we will make the case that Energy Audits are a primary foundation for smart capital investment as well as a source of O&M ideas. As a rule, audits are NOT the first thing to do in assessing performance and setting goals. Nonetheless, by logic and on the ENERGY STAR website discussion of Assessing Performance, audits are relevant to this part of our seminar.
We will give a specific definition of audit, developed by ASHRAE, and place audits in context for your energy management work.

## Slide 128
128
Assessing Performance and Setting Goals
A LEED Existing Buildings
Reference
PRINCIPAL CONTRIBUTORS
Michael Deru Richard Pearson Jim Kelsey
NREL Pearson Engineering KW Engineering
Notes: This reference is referenced by USGBC’s LEED® for Existing Buildings certification system. We’ll discuss the major elements covered by the manual.
The new edition of this book will appear in June 2011 (with a green cover).
128

## Slide 129: What is an Energy Audit?
An energy audit “…identifies and develops modifications that will reduce the energy use and/or cost of operating a building.”*
ASHRAE defines three levels of energy audit.
There are tasks and deliverables at each level.
129
*Procedures for Commercial Building Energy Audits (2011)
Assessing Performance and Setting Goals
Notes: As with many terms, some people will use “energy audit” loosely. The advantage of the definition and details provided by ASHRAE is that you can specify requirements for an energy audit, either as a customer or vendor.
129

## Slide 130
Objectives of an Energy Audit
Collect and analyze historical energy usage/cost
Study the building and its operation
Identify potential modifications
Perform an engineering and economic analysis
Prepare a rank-ordered list of modifications
Prepare a report/provide recommendations
Assessing Performance and Setting Goals
Notes: First few pages of the Procedures manual outline audit activities. This book, although small, is the best source of what is a Level I, II or III audit.
It is written in such a way that a person can use the descriptions in the book to ask in his RFP for a level II audit.
In the same way, a vendor can use the book to describe what they will do to conduct an Audit.

## Slide 131: What You Can Get…
Level I
  New ideas for low cost/no cost changes
  Ideas for capital changes
Level II
  All practical changes to procedures and settings
  List of capital projects; estimated costs and benefits
Level III
  Detailed economic and engineering basis for capital projects
Assessing Performance and Setting Goals
Notes: Additional notes:
Level 1 The advantage of a fresh perspective from a knowledgeable observer—can catch low cost/no cost ideas that have been invisible to people habituated to the building.
The main difference between Level II and Level III is the detailed observations and analysis to support recommendations and summaries for capital projects. In addition to on-site measurements of equipment and conditions, simulations will be included to build the case for specific capital projects. Interactions among components are considered (e.g. contribution of lighting load to heating and cooling requirements).

## Slide 132
Assessing Performance and Setting Goals

## Slide 133
133
Assessing Performance and Setting Goals

## Slide 134: Energy Audits and Capital Projects
Levels II and III give the economic and
engineering foundation for capital projects
  In the context of proper O&M procedures
  Understanding the organization’s capacity to incorporate the changes
Energy Audits II and III reduce the risk of unexpected results in capital projects
Assessing Performance and Setting Goals
Notes: Instructor will read the points.

## Slide 135: How You Can Use the ASHRAE Definitions of Energy Audits I, II, III
As a building owner :
Cite the definitions (cut and paste) for RFP
Compare vendor offerings to the definitions to negotiate proposed services
As a vendor:
Cite the definitions (cut and paste) in your responses to RFP
Use the outlines to organize your reports
Assessing Performance and Setting Goals
Notes: Instructor will summarize the functions of the Audit reference for two users, customers and vendors.

## Slide 136: Exercise 7: Audit Level Examples
Assessing Performance and Setting Goals
Page 19
in the exercises
Notes: Turn to page 23 in the Packet
Military Base:
Statement C is NOT clearly supported by the documentation but might be inferred from paragraph 4 .
You can find support for Statements A, B, D and E.
The simulation paragraph flags this audit as Level III.
Campus Building
Statements A, B, C and D are supported. There is no indication of energy simulations. Conclusion: Level II Audit.

## Slide 137: What About Commissioning?
Commissioning
Recommissioning
Retrocommissioning
Assessing Performance and Setting Goals
2015 ASHRAE Handbook—
HVAC Applications, Chapter 43
Notes: Commissioning: the process for achieving, verifying and documenting that the performance of facilities, systems and assemblies meets defined objectives and criteria.
Recommissioning: applies commissioning to a project that has been previously delivered using the commissioning process.
Retrocommissioning (existing building commissioning) applies commissioning to an existing facility that may or may not have been previously commissioned. It consists of systematically investigating, analyzing, and adjusting performance of existing building equipment, systems, and assemblies to ensure that required performance (including energy, comfort, and IAQ) are achieved.
These are great activities. If not properly linked to on-going, sustained energy management, commissioning can fall into the category of “occasional” O&M activities described by Christopher Russell.
(Source: 2007 ASHRAE Handbook—HVAC Chapter 42 page 42.1)

## Slide 138
138
ENERGY STAR Guidelines for Energy Management
www.energystar.gov
Assessing Performance and Setting Goals
Notes: In this section, we’ll touch on just a few slides related to goal-setting.
Setting clear and measurable goals is critical for understanding intended results, developing effective strategies, and reaping financial gains.
Too low a goal won’t inspire—you won’t build or maintain will to improve energy use
On the other hand, an unrealistic goal, unattained, can discourage or harm your career.
How can you set useful goals?
Practical advice: if you can see how to get 80% of the way to a goal in your time frame, go for it, you should learn along the way to pick up the other 20%. (citation: Kevin Little personal notes seminar with Y. Ando 1991, Japanese Total Quality Control Methods, crediting this advice to Kaoru Ishikawa.)
Data clues from your performance assessment can help you quantify the potential gain.
When you compare buildings, unusual performance of subsystems within buildings should guide your goal setting—your goal will have a firm foundation if it is based on comparisons to similar buildings and systems.
138

## Slide 139: Benefits of Goal Setting
Sets the tone for improvement
Basis to measure success
Helps the energy team to identify progress and setbacks
Fosters ownership, creates purpose, and motivates
Demonstrates commitment
Creates schedules and milestones
Assessing Performance and Setting Goals
Notes: Here’s the advice from ENERGY STAR--Setting goals helps the Energy Director:
Set the tone for improvement throughout the organization:
Measure the success of the energy management program
Help the Energy Team to identify progress and setbacks at a facility level
Foster ownership of energy management, create a sense of purpose, and motivate staff
Demonstrate commitment to reducing environmental impacts
Create schedules for upgrade activities and identify milestones
Energy Audits provide estimates of goals and measures to reach the goals. It is particularly useful to have specific goals for capital projects and to measure performance after upgrade.
For energy projects based on discretionary facilities operations, you can bootstrap your changes and your goal-setting.
Boot-strapping works well if you are able to measure short-term energy use (e.g. with sub-meters that produce 15-minute interval data.) You can try a change, check the impact, and then you will have some data to base your estimate of savings when the change is instituted permanently.

## Slide 140: Goals: Corporate Example
ENERGY STAR Partner: 3M
Energy Efficiency Goal: Improve global energy efficiency by 20% between 2006 and 2010, with 2005 as the baseline year. Efficiency will be calculated by dividing 3M net sales by 3M total energy use.
Progress: Through 2008, energy efficiency has been improved by 19.2%.
Assessing Performance and Setting Goals
Notes: You can apply the ENERGY STAR management cycle at the corporate level as well as the building level.
ENERGY STAR has examples of corporate goals and progress at http://www.energystar.gov/index.cfm?c=industry.bus_industry_goals
We will focus our discussion on goals at the building level, not the corporate level.

## Slide 141: Level II and III Audits: Ingredients for Goals for a Building
Assessing Performance and Setting Goals
Energy Efficiency Measure (EEM): AHU Variable Frequency Drives | Estimated Impact Calculation
Existing System Simulation | 843,961 kWh/year
EEM Simulation | 705,903 kWh/year
EEM Energy Savings | 138,058 kWh/year
EEM $ Savings | $22,918/year
EEM construction cost (Engineering not included) | $63,100
EEM Simple Payback | 2.75 years
Notes: Level II and III audits will contain specific estimates of energy savings. The predicted savings and costs are ingredients for the facility’s energy management goals.
This table comes from the Energy Audit report for Building 5679. Building 5679 had several EEMs recommended by the audit team, who were careful to discuss interactions and system level effects related to all EEMs being implemented simultaneously.
If you have an effective energy management system in place, you can (and should!) compare the predicted energy impact to the actual impact—though without specific sub-metering, it is challenging to verify the impact of each specific change.

## Slide 142: SMART Goals—Reminder
Specific
Measurable
Attainable
Relevant
Time framed
Assessing Performance and Setting Goals
Notes: There are many versions of SMART goals—this particular version comes from the open-source reference Wikipeida. http://en.wikipedia.org/wiki/SMART_criteria )
Note that the “Attainable” criterion is a PREDICTION that you can achieve the level of performance indicated by the goal.
You may shoot too low in your goal setting—particularly if your organization has the habit of criticizing any effort that does not make its numbers.
Goal setting related to discretionary facilities operations usually is more flexible than goal setting related to capital projects.

## Slide 143: Setting the Goal—Example
We will document 5% electrical energy savings over eight weeks at the Hilldale facility.
Table discussion: How SMART is the Great Dane goal?
Assessing Performance and Setting Goals
Notes: The Great Dane team came up with this goal based on their preliminary walk-through of systems. They focused on getting savings from wasted energy for lighting .
Using their facilities spreadsheet that listed lamps and operating hours, they had a pretty good sense that they could hit this mark.
The eight week time frame was based on a DOUBLING of the initial estimate that the operations changes in lighting and switching out some incandescent lights to compact fluorescent fixtures could be accomplished in four weeks. The facilities manager had many demands on his time and the team needed to recognize this constraint.
A specific goal helps keep the team focused, as ENERGY STAR advises.
Another guide for goal setting comes from the general numbers we presented earlier: Up to 15% of energy used in existing buildings is wasted and can be saved by no cost/low cost changes to operations.
For most buildings, this general value gives you an upper bound on your project estimates.
Does this goal meet the SMART criteria—Specific, Measurable, Attainable, Relevant, and Time-framed?

## Slide 144: Action Plans: Ideas and a Test Method
Now that I have a target building,
how do I start saving energy?
Action Plans: Ideas and a Test Method

## Slide 145
ENERGY STAR Guidelines for Energy Management
www.energystar.gov
Action Plans: Ideas and a Test Method
Notes: In terms of the Management Cycle, we now move from assessment and goal setting to putting a plan together to use energy more effectively in a facility.

## Slide 146
Two Types of Action
Discretionary facility operation
Capital improvements
Action Plans: Ideas and a Test Method
Notes: Capital Improvements are easy to grasp and get the attention of management because of the dollar costs associated with the investments.
We want to focus your attention on Discretionary Facility Operations. Why?
You can get started tomorrow
You don’t need a capital approval
Your work prepares for professional audits, retro-commissioning and recommendations for capital upgrades. Why not lay the groundwork so P.E.s are most effective and efficient?
After a capital upgrade or retro-commissioning, you need a test-and-monitor method to
  Verify results
  to hold the gains and
  continue to improve performance.

## Slide 147
147
Learning by Doing: “Reverse” Energy Audit Process
Low-cost actions decrease utility costs first
Knowledge and skill built by facility staff
In-depth audit and capital improvements follow, on firm foundation
Action Plans: Ideas and a Test Method
Notes: Here’s why we don’t recommend starting your Energy Management efforts with an Energy Audit—if you don’t have an energy management process in place, you have a weak foundation that will not take advantage of useful recommendations and won’t be able to verify performance of capital improvements.
When you operate the building differently and take low cost actions to reduce energy costs, you will often run into an obstacle. You then can apply capital improvements to remove these obstacles.
Learning (Trial and error, corrected) allows you to spend capital dollars after discovering the problems!
147

## Slide 148
148
“The most thorough energy conservation program begins at the end of each distribution system and works back to the Central Plant.”
- John Freund, John Deere Corp.
HPAC, September 1980, p.58
….So, start with end uses !
Action Plans: Ideas and a Test Method
Notes: John Freund’s observation frames the issue: improvement through discretionary facility operations start with
understanding energy end uses
Identifying wasted energy
Testing actions to reduce the waste
Observing impact of actions to verify that the actions were useful and did not compromise safety and the economic performance of the organization.
Another way of saying this key point (Jim Kelsey, KW Engineering)
"There are interactive effects among EEMs that may over or under estimate the savings for any individual EEM if some of the measures are removed from consideration. The sequence of measure implementation we use is that recommended by the California Energy Commission's Guide to Preparing Feasibility Studies for Energy Efficiency Projects, which recommends analyzing measure that affect load first, then work 'upward' from load to plant."
148

## Slide 149: A General Sequence of Systems to Tackle
Lighting
Fan systems
Pumping systems
Boilers and chillers
Easier to harder
Action Plans: Ideas and a Test Method
Notes: We have ranked the systems by the degree of technical complexity. Lighting systems typically are simplest to understand and to improve.
This is general advice. Of course, your specific actions will be based on your assessment of performance and you may choose to tackle the systems in a different order.
In the following slides, within each energy-using subsystem, we rank the ideas from easier to harder (more technically demanding to get things right).
START TAKING NOTES ON page 32 of the Exercises.

## Slide 150
150
Sample Discretionary Actions—Lighting
Match operating hours to activities
  Unoccupied lighting
  Existing custodial lighting
Take advantage of daylight
Check delays on occupancy sensors
Assure appropriate foot-candles for tasks (lumens)
Install high-Kelvin lamps
Easier to harder
Action Plans: Ideas and a Test Method
Notes: Operating schedule should match levels of occupied lighting.
Also, check appropriate levels and timing for
  Unoccupied Lighting
  Custodial Lighting
  Outdoor Lighting
Many older buildings are not designed to take advantage of daylight—glare can eliminate the possibility of harvesting effective light from windows. Buildings more than 50 years old may have larger windows that lend themselves to use of daylight (see Hitch School example, to follow.)
Timers and occupancy sensors require checking and maintenance. Standard settings from the factory may have longer durations than needed. Sensors fail for multiple reasons; do not assume that the sensors are functional without checking. In one small school (17,000 square feet), two out of three classroom occupancy sensors were not functioning correctly (and this was an Energy Star rated facility!).
Some areas may have more illumination than is required for tasks. You can check actual levels with a light meter; Portfolio Manager references the IESNA Lighting Handbook for lighting quality (http://www.ies.org/store/department/lighting-handbooks-10001.cfm).
By the way, a thorough lighting retrofit will include measuring ft candles to guide the correct number of lamps (rather than merely replacing old lamps fixtures with new lamps or fixtures.)
150

## Slide 151
151
Sample Discretionary Actions—Fan Systems
Match running time to activities
Lower hot-air temperatures
Raise cold-air temperatures
Lower fan pressure in ducts
Adjust static pressure set points
  Manual reset
  Dynamic reset using damper positions
Minimize outdoor air quantities
Minimize exhaust quantities
Match ventilation to number of occupants
De-energize exhaust fans and close OA dampers when unoccupied
Easier to harder
Action Plans: Ideas and a Test Method
Notes: Again, the easiest action to reduce fan energy is to match running time to activities.
Is the occupancy schedule aligned with activities? Does the system need as long a “warm-up” or “cool-down” period prior to occupancy?
The instructor will discuss examples of each of these actions.
151

## Slide 152: Major Tip
To warm or cool the building ahead of occupancy, be sure that outdoor air dampers are closed until occupancy.
Action Plans: Ideas and a Test Method
Notes: The key point here is that many systems ARE linked—when the system is actively heating or cooling, dampers are opened.
This linkage often adds energy burden as you need to condition the outside air as well as the inside air.
In winter, building can be heated up quicker if not bringing in outside air all night!

## Slide 153
153
Sample Discretionary Actions— Fan Systems (cont.)
Make best use of economizer operation
Eliminate simultaneous heating and cooling
Reduce airflow in constant volume (CV) systems
De-energize non-essential loads
Seal leaky ducts
Convert CV systems to VAV
Action Plans: Ideas and a Test Method
Easier to harder
Notes: In addition to the discretionary actions, we also must include a simple, low cost maintenance reminder:
Seal leaky ducts!
If you have taken all these actions, you may find that you have avoided the need to go from constant volume systems to variable volume systems!
153

## Slide 154
154
Sample Discretionary Actions— Pumping Systems
Match running time to activities
De-energize non-essential loads
Verify proper flow
  Throttle balance valves
  Trim pump impellers
Lower pressure set point to optimize variable flow
  Manual reset
  Dynamic reset
Convert CV system to variable flow
Action Plans: Ideas and a Test Method
Easier to harder
Notes: The instructor will discuss examples of each of these actions
154

## Slide 155
155
Sample Discretionary Actions— Boilers
Lower hot-water temperatures
If steam, lower steam pressure
Install modulating burners (linkage-less)
Optimize boiler sequencing
Minimize losses in de-energized boilers
Action Plans: Ideas and a Test Method
Easier to harder
Notes: The instructor will discuss examples of each of these actions
155

## Slide 156
156
Sample Discretionary Actions— Chillers
Match running time to activities
Raise chilled-water set points
Reduce condenser water temperature
Optimize cooling tower fan speed
Optimize chiller staging
Minimize chiller cycling
Reduce chilled-water flow
Action Plans: Ideas and a Test Method
Easier to harder
Notes: The instructor will discuss each of these actions.
Note: as a general rule, for every degree F you raise a chilled water temperature you use 1.5% less energy. If you reduce condenser water temperature by 1 degree F you use 1.5% less energy.
156

## Slide 157: ENERGY STAR IT Tools
Action Plans: Ideas and a Test Method
https://www.energystar.gov/products/low_carbon_it_campaign/power_management_computer
Notes: The set of tools avaiable on the ENERGY STAR site include an online savings calculator and energy management software, along with public domain/operating system solutions.
The website language is written in ways to relate to IT professionals so you don’t have to translate energy jargon into terms easy for your IT staff..
http://www.energystar.gov/index.cfm?c=power_mgt.pr_power_management

## Slide 158
158
Other Lists of Discretionary Opportunities
Chapter 36, “Energy Use and Management,” 2015 ASHRAE Handbook—HVAC Applications
ASHRAE Standard 100-2018, Energy Conservation in Existing Buildings
Action Plans: Ideas and a Test Method
Notes: Chapter 35, ASHRAE 2007 Handbook page 35.13 gives a basic list of discretionary opportunities relevant to both simple and complex buildings and
ASHRAE Standard 100-2006 gives a set of practical operations and maintenance items in these paragraphs, including many discretionary opportunities:
6.2 Building Envelope
6.3 HVAC Systems
6.4 Energy Distribution Systems
6.5 Domestic Hot Water
6.6 Lighting
6.7 Chilled Drinking Water
Paragraph 6.8.1 Basic Energy Management lists the fundamentals in smart energy use.
158

## Slide 159: Exercise 8: Ranking Discretionary Actions for Discussion and Application
Action Plans: Ideas and a Test Method
Page 28
in the exercises
Notes: Turn to page 32 in the Exercises.
Review the table of discretionary actions, identify the actions that you would like to discuss further and flag the actions that look promising in your buildings.
GIVE PARTICIPANTS ABOUT 3 minutes to review the checklist.
DE BRIEF:
1. Ask if there are any items for further discussion.
Follow up.
2. Ask for someone to volunteer their Notes, things to investigate in their building soon.

## Slide 160
BREAK!

## Slide 161: Handouts
Course exercises
“Focus on Energy” best practices spreadsheets
WA Energy Audit checklists
Advocate Healthcare EM operational checklists
Aurora walk-thru audit notes
Excerpts from ASHRAE Standard 100-2018
ENERGY STAR Guidelines for Energy Management
Notes: The key point here is that many systems ARE linked—when the system is actively heating or cooling, dampers are opened.
This linkage often adds energy burden as you need to condition the outside air as well as the inside air.
In winter, building can be heated up quicker if not bringing in outside air all night!

## Slide 162
Wisconsin’s Focus on Energy
Best Practices Spreadsheets
Action Plans: Ideas and a Test Method

## Slide 163
Wisconsin’s Focus on Energy
Best Practices Spreadsheets
Air handlers
Boilers
Chillers
Cooking
Domestic hot water
HVAC
Lighting
Miscellaneous equipment
Refrigeration
Action Plans: Ideas and a Test Method
163

## Slide 164
Air-Handlers Best Practices
Install variable-speed controls on air handler supply fan
Convert air handling system from constant volume to variable air flow
Convert dual duct or multizone air handling system to variable air flow
Install premium efficiency motors
Install high efficiency AC units or RTUs
Reduce outdoor air intake
Install night setback controls (heating season)
Install night setup controls (cooling season)
Action Plans: Ideas and a Test Method

## Slide 165
Air-Handlers Best Practices
Action Plans: Ideas and a Test Method

## Slide 166
Air Handlers Best Practices
Install variable-speed controls on supply fan
Action Plans: Ideas and a Test Method

## Slide 167
Air Handlers Best Practices
Dick’s Tips
Turn off unneeded exhaust fans
Do not open OA dampers until occupancy
Action Plans: Ideas and a Test Method

## Slide 168
Air Handlers Best Practices
Reduce outdoor air intake
Action Plans: Ideas and a Test Method

## Slide 169
Chillers Best Practices
High efficiency chillers
Chilled-water reset
Chilled-water pump VFD
Action Plans: Ideas and a Test Method

## Slide 170
Chillers Best Practices
Dick’s Tips
Increase chilled-water temperature: save 1.5% power per 1°F
Decrease condenser water temperature : save 1.5% power per 1°F
Extreme Example
Increase chilled-water temperature from 42°F to 48°F and decrease condenser water temperature from 78°F to 75°F:
Save 13.5% power
Action Plans: Ideas and a Test Method

## Slide 171
Chillers Best Practices
Chilled-water reset
Action Plans: Ideas and a Test Method

## Slide 172
Lighting Best Practices
Compact Fluorescents LEDs
LED exit lights
Reduced hours of operation
Occupancy sensors
Vending machines
T12 to high-performance T8s
Metal halide to high-performance T8s or T5s
Task lighting
Action Plans: Ideas and a Test Method

## Slide 173
Lighting Best Practices
Action Plans: Ideas and a Test Method

## Slide 174
Miscellaneous Best Practices
ENERGY STAR Computers and Monitors
Replace windows
Vending machine occupancy sensors
Add roof insulation
Reduce infiltration
Action Plans: Ideas and a Test Method

## Slide 175
Miscellaneous Best Practices (cont.)
Action Plans: Ideas and a Test Method

## Slide 176
Miscellaneous Best Practices (cont.)
Vending machine occupancy sensors
Action Plans: Ideas and a Test Method

## Slide 177
Wisconsin’s Focus on Energy
Best Practices Spreadsheets
Available in virtual handouts
Action Plans: Ideas and a Test Method

## Slide 178
ENERGY STAR Guidelines for Energy Management
www.energystar.gov
Evaluating Progress
Notes: Now that you have created an action plan and tried one or more ideas, you need to measure the results—did you get the improvement you predicted? If YES great, if NO, then do you understand what happened?
In many cases, if your change did not work well, your execution may have been weak—for example, the occupancy schedule did not actually get changed to match the true building schedule. If you don’t evaluate progress, you won’t catch simple failures.
Just as importantly, you may miss major issues in performance that affect credibility and confidence in your energy management.

## Slide 179
Funding a Retrofit
Property Assessed Clean Energy (PACE)
Financing tool for building owners to fund:
      Renewable energy
      Energy efficiency
      Water conservation
Financing payments covered by utility savings
Enabled by applicable state legislation
179

## Slide 180
100% Financing
PACE covers up to 100% of hard and soft costs of clean energy improvement
No money down
Replace equity or mezzanine financing with low cost non-recourse financing
Loan to Value
Why PACE?
180

## Slide 181
Cash Flow Positive
Long loan terms up to 20 years (30 years for solar).
Fully amortized.
This makes it possible for the annual utility bill savings to be greater than the PACE loan repayment.
Example: During the repayment term, the utility bills decrease by $20K annually; PACE repayment is $15K annually: Results in a $5K increase in NOI. This boosts cash flow and property value.
Why PACE?
181

## Slide 182
Why PACE?
Transferable: PACE is attached to a building, not an individual or business.
PACE tax assessments can be passed on to tenants under most lease forms.
Tenants save on energy costs and experience the same net payments, thereby reducing their occupancy cost (rent).
182

## Slide 183
Commercial PACE Programs Today
(Website http://pacenation.us/)
1063+ Projects $482+ Million 7,222 Jobs
183

## Slide 184
Measure Requirements
Useful life greater than five years
Permanently affixed to the property
Each improvement must
  reduce energy usage,
  reduce water usage,
  or generate renewable energy for the property
184

## Slide 185
Financing Terms
Loan Term: 5–30 years (full amortization)
Interest Rate: 350–450 bps over treasury (~6.00%–7.00%)
Loan Size: $100,000–$20.0 Million
PACE Loan-to-Value (LTV): 20%–30% (Total LTV: 95%)
Loan-to-Cost: 100%
Security: Tax assessment/special charge
Non-Recourse Financing
Loan To Value
185

## Slide 186
Fees
Program fee—charged at loan closing
  1% of PACE loan amount
  Minimum of $2000
  Maximum of $25,000
Commission fee—charged at loan closing
  0.10% of PACE loan amount
  Minimum of $50
Annual fee—charged with installments
  0.15% of outstanding principle balance
  Minimum of $250
  Maximum of $1000
186

## Slide 187
Property Owners Benefit
Financing for 100% of PACE Project cost
Long repayment periods: up to 30 years
Positive cash flow
Increase property value
Non-recourse financing (no personal guarantees)
Transfers to new owner upon sale
Tenants share cost and savings
Energy savings performance guarantees
187

## Slide 188
Introducing End-Use Evaluation
Use trend logs or portable data loggers:
Runtime
Temperature and humidity fluctuations
Electrical use
  Amps
  Watts
  kWh
Action Plans: Ideas and a Test Method
Notes: Here are the three uses we see as the starting point for end-use evaluation. Instructor will refer to the slide contents.
End use evaluation helps you
To verify that your building can benefit from the discretionary actions listed earlier
To check that the actions have worked or not, to allow you to adjust your implementation.

## Slide 189: Trend Logs from Control Systems
Action Plans: Ideas and a Test Method
Notes: This shows a zone temperature trend log from a web-based building control system.
Building Control Systems can guide and support sustained energy management if used to their potential.
Many systems are now available with web interfaces allowing energy managers and teams to get information easily.
One feature to explore: check to see how you and members of your energy team can access the Building Control Systems with “view only” credentials—these users will not be able to change set points or other parameters but will be able to see trend graphs and data values to guide energy management actions.

## Slide 190: Stand-alone Loggers (Download Data to Analyze)
Motor On-Off Logger (R) Temp/RH/Light Level (L)
Action Plans: Ideas and a Test Method
Notes: Inexpensive stand-alone loggers are easy to deploy and use. The loggers typically come with software to graph and tabulate the values—data interpretation does not require advanced technical training.
High school students have used these kinds of loggers successfully to study building performance.

## Slide 191
Action Plans: Ideas and a Test Method
Notes: The instructor will explain this application—it shows the results of a portable data logger on a valve, in a restaurant. You can see the opening and closing short time intervals for a long time.

## Slide 192: Boiler Fire Rate Versus OA Temperature
Action Plans: Ideas and a Test Method

## Slide 193
Action Plans: Ideas and a Test Method
Notes: This is an example of an “on-off” logger tracking a kitchen exhaust system. According to the cook, the exhaust system are turned on and off every day.
The facility was unoccupied on weekends, so exhaust system should be turned off! And in fact, staff claimed that they were quite consistent in turning the system off on weekends.
The monitor shows ON OFF on the graph. There was a series of weekends when it was OFF then OFF, then OFF, but then ON and ON.
You can compare the story that staff says is the case to the story of what really happens, told by a simple data-logger.

## Slide 194
Office Temperature/RH—Verex
Action Plans: Ideas and a Test Method
Notes: The instructor will explain this application.
Here is another office example.
What we learned: temperature is fluctuating two or 3 times a day, 4 or 5 degrees, never drastic, never fast, but indeed fluctuating.
The story regarding the fluctuations: the people in the office thought they had bad indoor air quality. They experienced discomfort, with symptoms of upper respiratory problems. People wondered if the building had mold problems.
The engineers discovered the Temp fluctuations, and then calibrated equipment to prevent the fluctuations. A few months later, the cases of upper respiratory complaints and poor indoor air quality had disappeared. No mold! People were made uncomfortable by the temperature changes,
This example is not strictly about energy management but does show how useful loggers can be.

## Slide 195
Bank Temperature/RH
Action Plans: Ideas and a Test Method
Notes: The instructor will explain this application.
Data loggers mounted in branch bank in Okinawa, about 3 pm.
This building had very high RH, and so was very uncomfortable for occupants.
After 3 pm, we reduced air flow by manual damping. This physical change accounts for the changes in measured RH and RA Temp.
The cooling valve opened and brought the temp back up to 65.
When the air flow changes, the RH began to drop. The lights were turned off, cooling started to overcool the space. Them RH began to rise.
The top curve is the air delivery temperatures The difference between the space temp and the delivered temp was low, therefore no moisture removed.
In the morning, changes seen in the curves as the system moves to occupied mode and people arrive.
The SA temp drops and relative humidity drops well below previous levels.
So this case shows how you could use three simple data loggers to prove that less air flow will drop relative humidity significantly—with reduced energy use and improved comfort.

## Slide 196
Bank ∆T Versus %RH
Action Plans: Ideas and a Test Method

## Slide 197: Cooling Coil Rules of Thumb
DT of Air Moisture Removal
5° to 8° zero
8° to 12° barely measurable
12° to 16° good
16° to 20° excellent
Action Plans: Ideas and a Test Method

## Slide 198: Case Exercise 9: Using Motor Logger Data
Action Plans: Ideas and a Test Method
Page 30
in the exercises
Notes: Turn to page 34 in the Exercises.
Energy savings: 10 hours a day @ 3 kW = 30 kWh per day x 365 days per year = 10950 kWh per year.
Dollar savings: 10950 kWh @ $0.10/kWh = $ 1095.00
CO2 savings: 21,900 lbs CO2 (10.95 tons)

## Slide 199
Disincentives for the Building Engineer
Risk of occupant discomfort
Risk of equipment failure
Experimentation can be terrifying
Action Plans: Ideas and a Test Method
Notes: The disincentives to change are real but they need not stop you. You do need to acknowledge these disincentives and overcome them.
There are all kinds of reasons why people are not enthusiastic about experimenting.
People who operate buildings are into routines. We on the other hand are asking them to experiment! This can be terrifying for many people.

## Slide 200
Incentives for the Building Engineer
Regular monitoring by the manager
Managerial encouragement to experiment
  Occasional, brief discomfort is OK
Teamwork
Accomplishment—getting results
Perks paid for by savings
Action Plans: Ideas and a Test Method
Notes: Just as there are disincentives, there are incentives that can be put in place. These incentives do not occur naturally—they require leaders and managers to create these incentives.
These incentives are part of the MANGEMENT changes to achieve sustained energy management.
For example, regular monitoring by the manager shows practical commitment to energy management—how time is spent by people reflects their practical priorities. Now there is technology to help you monitor—not like the Energy Management 101 example that relied on manual readings.
Regular monitoring communicates that taking action, supported by data, is important to the manager. Otherwise, the building engineer in many cases will find other tasks to do.

## Slide 201: So, if the Risk of Change is Worrisome…
Take small steps that are reversible.
Study your results, communicate, and adjust as needed.
Engage your boss and occupants in the tests.
Action Plans: Ideas and a Test Method
Notes: It you find yourself in conditions where you carry out a small scale test, think of limiting your tests in time (e.g. for one day) and extent (e.g, number of degrees of set point change or time devoted to warm-up cycle).
In other words:
  If you think the test should run for one week, what you could learn from one day test? A One hour test?
  What is the smallest change in set point or control that you can manage?
No matter what the scale of your test, get ready to study the results. You need to be prepared to compare your predicted outcome to actual results, using data on how well the test worked, including reactions of occupants.
In many organizations, it helps to communicate tests of change, as part of occupant education about energy management and to invite participation.
Often, people if asked “Are you willing to experience the change for one day?” will say “Yes.” It’s not so much that people resist change, they resist having changes imposed on them.

## Slide 202
BREAK!

## Slide 203
Evaluating Progress
Evaluating Progress

## Slide 204
ENERGY STAR Guidelines for Energy Management
www.energystar.gov
Evaluating Progress
Notes: Now that you have created an action plan and tried one or more ideas, you need to measure the results—did you get the improvement you predicted? If YES great, if NO, then do you understand what happened?
In many cases, if your change did not work well, your execution may have been weak—for example, the occupancy schedule did not actually get changed to match the true building schedule. If you don’t evaluate progress, you won’t catch simple failures.
Just as importantly, you may miss major issues in performance that affect credibility and confidence in your energy management.

## Slide 205
205
Why Commit to Energy Management?
Greener Pastures with Energy Savings
Emissions Reduction at Madison College
The above energy savings were achieved with an additional 700,000 ft² conditioned space!
Source: Madison College Engineering Manager. Wesley Marquardt. wmarquardt@madisoncollege.edu.
Notes: This slide illustrates the conversion of energy savings into environmental impact.
You can convert savings of energy into emissions using factor tables produced by the EPA and the Department of Energy.
The calculations of emissions in this slide come from Emissions Factors and Energy Prices for the Cleaner and Greener Environmental Program
http://www.cleanerandgreener.org/download/efactors.pdf which has emissions factors by state.
Also, the EPA eGRID program has similar information, on a state by state and power plant basis, http://www.epa.gov/cleanenergy/energy-resources/egrid/index.html
ENERGY STAR’s Portfolio Manager on-line program will calculate the emissions for your buildings automatically so you can let ENERGY STAR do the emissions arithmetic for you! We’ll discuss the Portfolio Manager tool later this morning.
The impact on environmental emissions is impressive, equivalent to more than 800 kW of PV production in the upper Midwest.
MANAGEMENT NOTE: Wes reduced the energy use in the face of increased program demand and increased square footage.

## Slide 206
Greener Pastures with Energy Savings
Energy Cost Avoidance at Madison College
Notes: This is a key slide for your understanding. The MYTH described by facilities manager Wes Marquardt is believed by many people and can be a huge source of argument and disappointment. You need to understand the difference between “extra money” and “avoided costs.”
Your energy savings may not yield extra dollars to spend--the savings may only have avoided even higher bills.
You see the EUI (kBTU s/f) dropping steadily across the six year period. Energy bills (green shaded area) keep rising!
Over the six year period, energy costs per BTU rose about 40%.
Cost Arithmetic
Electric Utility rate 2001: .0508 dollars per kWh
Electric Utility rate 2006: .0747 dollars per kWh (source Madison Gas & Electric Company rate sheets)
Natural gas prices:
2001/2 average 0.60 dollars per therm
2006/7 average 1.0 dollars per therm
(source http://tonto.eia.doe.gov/dnav/ng/hist/n3020wi3m.htm )
Energy prices increased close to 40% over four years.
In the analysis, current dollars were used. Adjusting for inflation (putting all dollars on the same basis) can help make financial analysis more meaningful.

## Slide 207
Honolulu Office Building: Before and After
Evaluating Progress
Notes: Here is the Honolulu example after operations changes and a capital upgrade.
We have two more daily profiles, after the changes, added to the original graph. The building automation system was smarter than the time clocks and programmed not to start until 5 a.m.
New chillers and new pumps were installed….as time progressed, energy use comes down.
The difference between upper and lower curves is $100,000 a year. Expenditure was $500,000.
The unknown energy use (base demand of about 200 kW) has still not been addressed.
This is the value of interval data to see how you are doing and what else may still need to be done. So don’t forget to evaluate!

## Slide 208
Honolulu Office Building: Before and After
Evaluating Progress
Shaded Area = Energy Savings = $100,000/yr
Notes: Here is the Honolulu example after operations changes and a capital upgrade.
We have two more daily profiles, after the changes, added to the original graph. The building automation system was smarter than the time clocks and programmed not to start until 5 a.m.
New chillers and new pumps were installed….as time progressed, energy use comes down.
The difference between upper and lower curves is $100,000 a year. Expenditure was $500,000.
The unknown energy use (base demand of about 200 kW) has still not been addressed.
This is the value of interval data to see how you are doing and what else may still need to be done. So don’t forget to evaluate!

## Slide 209
What We Did
Operational changes—matched schedules to occupancy
Capital—more efficient chillers, pumps, towers; new building automation system to integrate equipment operation
Cost of changes paid back in five years from savings
Evaluating Progress
Notes: Instructor refers to slide points to summarize the changes to the Honolulu office building.

## Slide 210
Honolulu Office Building:
Energy Management Results
20% energy savings
Savings per year:
  $100K
  750 tons carbon dioxide (CO2)
  2.3 tons nitrogen oxide (Nox)
  2.0 tons sulfur dioxide (SO2)
.
Notes: Instructor will summarize the impact—energy, dollars, environmental—reminding participants that it helps to express the impact in all three ways.

## Slide 211
Madison Insurance Company
Evaluating Progress
Notes: Instructor will discuss the situation at this company, multi-facility campus.

## Slide 212
Madison Insurance Company:
Evaluate Progress
Evaluating Progress
Notes: Instructor will ask the audience to interpret this graph of progress.
Each colored line represents a different year; peak demand was reduced over 20%.

## Slide 213
Madison Insurance Company:
Evaluate Progress
4.1 million kWh per year
provides electricity for 586 new homes!
Evaluating Progress
Notes: The annual profiles show the change, with reduced energy use over time., also about 20% lower than at the beginning of the effort.
We translate the energy change from baseline into units that are easier for most people to understand: homes.
In this case the senior managers are proud to tell the community about their energy savings, expressed in numbers of homes.
Here, we used a figure of about 600 kWh per month (7200 kWh per year) as typical electricity use for a residential customer in the Upper Midwest.
You can get figures from your local utility if you want to translate your energy savings into “home” units.

## Slide 214: Madison Insurance Company
Operations changes: matched energy use to occupancy and needs
  Reduced fan energy
  Reduced pump energy
  Reduced lighting energy
Capital upgrade: lighting retrofit
Evaluating Progress
Notes: Instructor will add details to the items on the slide.

## Slide 215
Assessing Performance and Setting Goals
GSA Energy Management Program: The Rest of the Story
U.S. courthouse
Jacksonville, Florida
Energy improvements
DOE-ORNL Report
Notes: Here is a continuation of the Courthouse story, now with the addition of the ENERGY STAR score that you can now understand.
The building was predicted to be better than 79% of courthouses and eligible for the ENERGY STAR 75+ Plaque on the wall.
Much worse—59% of courthouses perform better!

## Slide 216
Assessing Performance and Setting Goals
2000s New Building Performance
Far less efficient than design intent
Notes: Here is a continuation of the Courthouse story, now with the addition of the ENERGY STAR score that you can now understand.
The building was predicted to be better than 79% of courthouses and eligible for the ENERGY STAR 75+ Plaque on the wall.
Much worse—59% of courthouses perform better!

## Slide 217
Assessing Performance and Setting Goals
EEMs Implemented
VAV minimum settings reduced to 10%
Boilers turned off in summer
AHU duct static pressure set points reduced from 1.5 in. wc to 0.7 in. wc
Notes: Here is a continuation of the Courthouse story, now with the addition of the ENERGY STAR score that you can now understand.
The building was predicted to be better than 79% of courthouses and eligible for the ENERGY STAR 75+ Plaque on the wall.
Much worse—59% of courthouses perform better!

## Slide 218
Assessing Performance and Setting Goals
Results of Control Modifications
Energy Savings: 18.7 trillion Btu/year
Cost savings: Over $200,000/year
ENERGY STAR plaque is now in the lobby!
Notes: Here is a continuation of the Courthouse story, now with the addition of the ENERGY STAR score that you can now understand.
The building was predicted to be better than 79% of courthouses and eligible for the ENERGY STAR 75+ Plaque on the wall.
Much worse—59% of courthouses perform better!

## Slide 219
Downtown Chicago ENERGY STAR Building
Uninsulated concrete,
single-pane glass
Evaluating Progress
Notes: 30 year old building—envelope poor!
New chiller, somewhat efficient (hoisted by helicopter)
Not shown: New boilers—most efficient condensing boilers
Not shown: New energy mgt system
Not shown: new variable speed fans
Building engineer—had routines for everything. Started to experiment with the new building mgt system. The engineer who designed it encouraged the building engineer to experiment.
Energizing fans closer and closer to occupied start time.
New Hot water system was more efficient with lower water temp. Started to lower water temp!
Perimeter baseboard heat. Old fashioned variable volume system with integral controls, occasional malfunction. “But the last time I lowered it, too cold in a couple of floors on the west side. Engineer said go check the valves sticking open. “
With all these changes, the gas bill did NOT go down in the winter.!!! The engineer was stumped, “What the HECK????? “ Six months later, People’s Gas sent a rebate for $50,000 after reading estimated bills all winter.

## Slide 220
Madison Bank
Evaluating Progress

## Slide 221
Annual Profile of Monthly Peaks, kW
Chillers add 500 kW in summer
Evaluating Progress

## Slide 222
Annual Profile of Monthly kWh
Fans waste energy in winter!
Evaluating Progress

## Slide 223
Evaluate Progress Three Years Later
Energy management did not work !
Evaluating Progress

## Slide 224: Explanation of No Progress at Madison Bank
The high electrical energy use in colder months results from decision to maintain fans on 24/7:
  No commitment to improve energy use
  No accountability
Therefore, no change
Evaluating Progress
Notes: Despite correct engineering analysis and evaluation of wasted energy, documented in a consulting report, nothing changed.
If responsible managers are not interested and do not organize their staff to manage energy intelligently, do not expect your insights to make a difference.
In terms of our basic ingredients for change (Will, Ideas, and Execution), the consulting engineer finds Will the most difficult one to build up.
For external consultants, you have some freedom to choose your clients. For internal staff, you may still be able to demonstrate the potential for energy management by specific tests, though it will be tough to sustain efforts.

## Slide 225: But Things Have Changed!
Chart: US Bank Plaza - 1 S. Pinckney Electricity Use (kWh) Comparison
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
1998 | 765000 | 645600 | 681000 | 619200 | 653400 | 678600 | 770400 | 702600 | 741000 | 596400 | 537000 | 630600
1999 | 784200 | 607800 | 640200 | 605400 | 584400 | 679200 | 747600 | 762600 | 603600 | 601200 | 586800 | 718800
2000 | 742200 | 698400 | 612600 | 622200 | 702600 | 657600 | 763800 | 656400 | 684000 | 604200 | 614400 | 795600
2001 | 776400 | 688800 | 654000 | 716400 | 624000 | 606000 | 765000 | 701400 | 663600 | 615600 | 570000 | 591600
2002 | 772800 | 714600 | 637607 | 699742 | 611437 | 627835 | 789876 | 697786 | 698256 | 632620 | 609871 | 688866
2003 | 776396 | 638202 | 632734 | 693350 | 685157 | 352544 | 744926 | 693435 | 732055 | 566155 | 486337 | 706433
2004 | 729880 | 684654 | 596953 | 718808 | 594560 | 639467 | 691320 | 656109 | 693881 | 586078 | 537428 | 624198
2005 | 676748 | 680565 | 624049 | 644364 | 570403 | 688990 | 750716 | 707499 | 722305 | 607541 | 596322 | 666869
2006 | 732662 | 639825 | 636592 | 644041 | 614770 | 701630 | 750433 | 677192 | 672244 | 560767 | 681299 | 659096
2007 | 665015 | 697775 | 609052 | 676582 | 533082 | 634304 | 707090 | 671357 | 669151 | 587424 | 672356 | 628383
2008 | 729191 | 679425 | 661413 | 611561 | 559548 | 610509 | 671247 | 679504 | 657554 | 576922 | 548686 | 615175
2009 | 730879 | 589150 | 566069 | 637115 | 430904 | 398771 | 470571 | 416623 | 393825 | 326152 | 301279 | 310596
17 day bill period
August 2010: New tenants include 11,000 ft2 restaurant
Evaluating Progress
Notes: A new owner and a new facilities manager have dramatically changed energy use.—from capital investment in new chillers and pumps, took better control of air terminal devices and reduced fan static pressure. Fan energy is a major component of the change. He found another source of waste, electric resistance heaters running in the ductwork.
The manager wrote us on 19 Nov 2010: “Our usage has actually increased from last year, due to the addition of the L’etoile and Graze restaurants. When I remove their usage (which we submeter and track), our usage is actually less than the same period last year. Those new restaurants use about 36,000 KWH per month. That equates to about $4.50 PSF for their combined 11,000 SF. BIG restaurants, 18 hours per day at Graze.
So, the fact that minus their usage, we are still lower, is a great thing. Consider that we have added about 13,000 SF of other office tenants since last year, and energy use is still less.”

## Slide 226: U.S. Bank Gas Utility Analysis
Year | Gas Usage, therms) | Gas Cost, $ | Gas Rate, $/therm
2002 | 172,220 | $87,236 | $0.51
2011 | 101,556 | $70,713 | $0.70
Reduction | 70,664 (41%) | $16,523 (19%) | +$0.19
Evaluating Progress

## Slide 227
Evaluating Progress

## Slide 228: US Bank Electric Utility Analysis
Year | Electric Usage, kWh | Electric Cost, $ | Electric Rate, $/kWh
2002 | 8,181,296 | $523,405 | $0.064
2011 | 4,282,613 | $489,521 | $0.114
Reduction | 3,898,683 (48%) | $33,884 (6.5%) | +$0.05
Evaluating Progress

## Slide 229: US Bank Electric Demand Analysis
Year | Max Electric Demand, kW | Min Electric Demand, kW
2002 | 1979 | 1430
2011 | 1433 | 724
Reduction | 546 | 706
Evaluating Progress

## Slide 230
Evaluating Progress

## Slide 231: US Bank Asset Value Example Using a 7.6% cap rate
2002 costs minus 2011 costs
Total savings = $50,407
$50,407 ÷ 0.076 (cap rate) =
$663,250 increased asset value
Evaluating Progress

## Slide 232
Results of Pilot Project at Waukesha Memorial Hospital
Collected 2005 utility information
  30-minute electric
  Daily natural gas consumption
Plotted daily consumption versus outdoor air temperature
  Established a model of building with weather normalized
  Weekend usage slightly different than weekday usage
Evaluating Progress
Notes: The instructor will illustrate an approach to using weather-normalized data to track the impact of changes at a daily level, much more sensitive than the monthly adjustment just shown.
In this case, the hospital had daily logs of natural gas use; it is relatively unusual to have interval data for your gas meters.
Interestingly, even though the hospital operated 24/7, we could distinguish weekday and weekend use in our analysis.

## Slide 233
Daily Data: Results of Pilot Project
at Waukesha Memorial Hospital
$90,000 annual savings in natural gas use
Adjustments to steam pressure and fine-tuning of burners on boilers—no capital!
Data provided clues to changes in operations
Evaluating Progress
Notes:   Here are the data analysis steps we used:
  Plotted daily consumption versus outside air temperature to model energy use, accounting for weather
  Compared model predictions to actual use and looked for anomalies
  Asked questions, found ideas for changes that would account for the patterns we saw
  Tried the changes to confirm that they worked (by looking at impact on energy use)
  The adjustments to the system were relatively minor and so there was excellent financial return on investment in this case.

## Slide 234
OA Temp < 48°F
Y=54,578
OA Temp > 48°F
Y=998.16*X + 6,667
Excel® can give these kind of formulas, if you have a bit of knowledge!
Evaluating Progress
Notes: This is weekday electric use. Each point on the graph is one day’s kWh use vs the average temperature for that day.
If you enter the daily records of kWh use and average temperature, row by row, in Excel and plot the kWh values versus the temperature values, you get the plot without the extra lines.
We did a little extra work to get the lines--There are really two fits to the data, one is a flat line, which indicates that until the hospital needs mechanical cooling at about 48 deg F, electricity use is essentially constant (horizontal line.) Above 48 deg F, electricity use increase at about 1000 kWh for every degree increase.
Excel can tell you the equations if you click the appropriate functions.

## Slide 235
Evaluating Progress
Notes: Here’s the corresponding graph for gas use.
Now each point is daily CCF (hundred cubic feet, approximately a therm) plotted vs the average temperature for that day.
The cloud of points has some curvature, so in this case, we used a simple exponential function to approximate the shape of the data.
Using the baseline curves for gas and electricity use, we built a spreadsheet that would predict energy use, given outside air temperature, day by day.

## Slide 236
Discretionary Operations Changes to Improve Gas Use
Lowered steam pressure, in steps
  Starting pressure was ~120 psi
  Tested reductions in steps of 10 psi
  Settled on new level: ~90 psi
Fine-tuned burners
Evaluating Progress
Notes:   As we watched the spreadsheet, day by day, the engineer started doing things.
  We could not lower pressure all the way to target (~65 psi, minimum required so sterilizers will function) because one section of the building would not work at pressure lower than 90 psi.
  This was discovered as the pressure was lowered below 90 psi and reports back to the building engineer indicated problems.
  This is an important example of TESTING a change and adjusting in light of feedback from occupants.

## Slide 237
7% Savings in 12 Months: $89K and 530 Tons CO2
Evaluating Progress
Notes: This is how the spreadsheet works, manual process in this case.
Gas meter is read to give us the actual gas consumption for the day.
As soon as we have the average Temp for a day, the spreadsheet calculates the predicted gas energy using our baseline curve.
In the display, we cut out the middle pages of the data,--we show our start in Jan 06 and our end in Dec 06.
We show that gas consumption is 93% of the previous year, already accounting for temperature. This is large building, 89000t herms @$1 a therm.
So paying attention to a few things, we were able to save $90K and 530 tons of CO2 emissions, with no capital expenditures.

## Slide 238
Extra Benefit: An Energy Management Breakthrough
Evaluating Progress
Notes: The day by day monitoring had an extra benefit.
In Fall 2006. when outside air T was around 50, some days it would be cool enough for outside air to cool the building. Some times large chiller would start.
In the middle of the period, the building was operating at less than 100%--more efficient than predictions based on the model year.
Then for a few days, the energy use jumped above 100%--related to a weekend!
The building engineer came in on Monday and found he was over 100% on gas consumption, he knew of no changes, and wasn’t sure what was happening. He had a discussion with his staff and discovered the big chillers were going on and off in the fall weather. To prevent this cycling, staff had made over-ridden controls and the chillers were running constantly….so the additional gas consumption was from chillers running,coupled with the hospital’s constant volume air system, the gas was being used for reheating.
Now, the values are relatively small--the difference between predicted and actual, a few hundred therms a day. Values this small compared to 1,000,000 therms a year would be buried in monthly data.
This example illustrates the value of paying attention on a frequent basis.

## Slide 239: Applying the Process
Aurora Health Care—2009
17 facilities
7 million ft2
Each facility joined the Portfolio Manager® system
President of Aurora Healthcare signed an ENERGY STAR commitment to reduce energy 12% in three years
Each facility utilizes the spreadsheet and records energy consumption daily
Monthly summaries distributed to all
Monthly energy initiative meeting to share successful ideas
Evaluating Progress

## Slide 240
Aurora Sinai Medical Center
Daily Utility Tracking Spreadsheet
Evaluating Progress

## Slide 241
Aurora Sinai Medical Center
2009 Utility Summary
Energy Savings:
19% reduction in steam usage
6% reduction in electrical usage
Evaluating Progress

## Slide 242
Aurora Health Care 2009–2012 Utility Summary
Savings:
14.8% reduction in energy usage
92,509 tons reduction in CO2 emissions
NEW
Evaluating Progress

## Slide 243
Aurora Health Care 2009–2011
14.1% reduction in energy consumption
142.6 million pound (64,669 metric tons) reduction in CO2
Three facilities achieved ENERGY STAR
Evaluating Progress

## Slide 244
Evaluating Progress
Additional Energy
Management Breakthroughs

## Slide 245
BREAK!

## Slide 246
Source: Corporate Realty, Design & Management Institute.
Evaluating Progress

## Slide 247: Aurora Health Care Equivalent Revenue (Using a 4% Margin)
2009–2012 Total Energy Savings (weather-normalized)
Total Savings = $8,665,000
$8,665,000 ÷ 0.04 (margin) =
$216,625,000 equivalent revenue
$216,625,000 ÷ 4 years =
$54,156,250 Equivalent Revenue per Year
Evaluating Progress

## Slide 248: Energy Management Strategies Taken
Chiller operations
HW reset schedules
Run schedules (occupied/unoccupied, day/night, summer/winter)
DA temperature reset schedules
Steam pressures
Installation of variable-speed drives
Steam trap survey
Shutting off air handling units in unoccupied areas
Maintaining modified space temperatures
Promoting the energy message at department meetings
Evaluating Progress

## Slide 249: Outdoor Air Temperature Data Sources
Sources | Barriers to Use
Outdoor air sensors—BAS | Extracting data; maintenance of sensors; data quality
Stand-alone temperature sensors | Extracting data; maintenance of sensors; data quality
NOAA data (public domain) https://gis.ncdc.noaa.gov/maps/ncei#app=cdo | No cost for simple searches; cumbersome to access multiple locations
Weather data services | Fee for access to comprehensive database
Weather Underground https://www.wunderground.com/history/ | No cost for searches; long time periods require multiple searches
Evaluating Progress
Notes: Here are four sources of temperature data that you can use for weather normalization.
http://www.weather.gov/climate/ is the portal to access reports from NOAA weather stations.

## Slide 250: Energy Management: Accountability Revisited

## Slide 251: Accountability
A person is accountable; a department or building can’t be!
Accountability : Key to Energy Management
Notes: In this last section of the seminar, we return to the key point we started with, accountability.
Accountability means a specific person owns the results of the actions to manage energy (good, bad or not done at all.)
I have learned that all the good ideas --to upgrade O&M practices, to use data for energy detective work, to understand the impact of weather—all of these are just good ideas unless you have accountability to put them into practice.
Everything we have discussed today is just theoretical unless there is a person accountable—somebody must be accountable.

## Slide 252
Lowell Hall Facility— What’s Missing?
Accountability : Key to Energy Management
Notes: We will give you a quick review of the Lowell Hall case—
The Lowell Center is a multiple use building of 118,000 gross square feet with seven floors, plus an occupied basement level. The building was constructed in 1959, with a major addition in 1966. The building houses university faculty and administrative offices, classrooms, and a hotel function, complete with an indoor swimming pool and banquet dining for out-of-town seminar attendees.
Building heat, pool heating, and the bulk of domestic water heating is furnished by two, gas/oil scotch marine type fire tube hot water boilers. A small gas-only boiler provides summertime heat for domestic hot water and to heat the swimming pool. A gas fired commercial type water heater furnishes 180°F water for the final rinse of the dishwasher.
Cooling is furnished by two electrically powered water chillers, each serving separate portions of the building. Heating water and chilled water are utilized in 35 individual air handling systems serving various portions of the facility. Air handling system operation is intended to be scheduled by an energy management system.
The building has had major investments (capital projects) over its life time.
Lowell Hall has not reaped the benefit of these investments because there is no commitment to energy management.

## Slide 253: Facility Upgrades
Change | When
Efficient central water chiller | Summer 1995
Lighting upgrade (T8, elec ballasts) | Spring 1996
Cooling tower replacement | Spring 2000
Building automation controls | Spring 2000
Heating water pumps modification to AHU | Summer 2003
Remodel of lobby, HVAC upgrade | Summer 2006
Accountability : Key to Energy Management
Notes: The facility owners have invested significant funds to the building. The Heating Pump modification aimed to increase the volume of outside air but the system is not well managed across seasons.
The upgrade to the Building Automation controls did not yield its potential. In the audit of the facility, the auditors found that the system is not programmed to schedule the operating times of connected loads. The auditors believe the facility could save at least $10,000 per year by entering schedules into the new system, which should cost very little.

## Slide 254
Lowell Hall Energy Performance
Accountability : Key to Energy Management
Notes: Portfolio Manager shows that with the snapshots separated by 9 years, Lowell Hall is moving in the wrong direction.
What does the energy history reveal?

## Slide 255: History Matches Portfolio Manager
Accountability : Key to Energy Management
Notes: Here’s a view of energy history for 19 years. The plots over time are consistent with the snapshot presented in the two point comparison provided by Portfolio Manager. No dramatic improvement in energy use.
The changes related to lighting appear to have reduced demand by about 20 kW. Electric energy use increased after the lighting upgrade.
2006 was a particularly mild winter in Wisconsin. Let’s take a quick look at weather adjusted data for the site.
(A legitimate issue with long time series analysis of a building’s energy use: how have patterns of use changed that might account for the change in energy? The general programming at the building has stayed relatively constant over the past decade. An energy management system would note changes in use and then be prepared to normalize energy use for increased service. Note that Portfolio Manager accommodates hours of use in its calculations of ENERGY STAR ratings. The instructor will address this issue.)

## Slide 256: Lowell Hall—Gas Usage
Accountability : Key to Energy Management
Notes: Instructor to explain the curve, after asking for a volunteer in the audience to explain the analysis.

## Slide 257
Accountability : Key to Energy Management
Notes: Interpretation of the curves reveals a current baseline (non-weather) energy use of over 3,000 kWh per day. The trend line of 1990 data indicates original baseline energy use of less than 2,500 kWh per day. Energy use has INCREASED during this period.

## Slide 258: Lowell Hall Evaluation
Score on our Energy Management checklist:
1 YES 14 NO No Bonus Points
Accountability : Key to Energy Management
Notes: When you run through the Energy Management Checklist (from Exercise 1), there is no evidence of practical management of energy by Lowell Hall staff.
The only point that gets a YES is question 1: energy use is measured monthly because the building is separately metered by the utility and the measurements are available in the accounting department.
The absence of energy management at Lowell Hall goes a long way towards explaining the history of energy use and the failure to take full advantage of the capital upgrades.

## Slide 259
Energy Management at
Monona Terrace Convention Center
Jeff Griffith
Building Maintenance Supervisor
      Action plan
      Monitoring
      Benchmarking
      Accountability
Accountability : Key to Energy Management
Notes: We want to contrast the situation at Lowell Hall with the situation at the Monona Terrace Convention Center, Madison, WI.
Jeff Griffith plays a central role in the development of Energy Management, with the ingredients listed on the slide. Jeff did not follow the exact sequence outlined in the ENERGY STAR flowchart, he followed his own logic.

## Slide 260: Action Plan
Initial commissioning by staff
No compromise in customer comfort
Eliminate simultaneous heating and cooling
Adapt operation to daily schedule
Eliminate energy use in unoccupied spaces
Regular reminders to entire staff
Accountability : Key to Energy Management
Notes: Instructor to refer to slide content.

## Slide 261: Regular Monitoring
Weekly energy review by engineering staff
BAS alarms to pagers
      Demand exceeds 1100 kW
      Chilled water exceeds 50°F
Personal attention by one engineer on peak days
Accountability : Key to Energy Management
Notes: Instructor will review slide contents.
There are many alarms that could go off—they have restricted HIGH LEVEL alerts to just two, only the first of which is strictly speaking energy management. The second deals with comfort of patrons.
The point of this slide is that they have thoughtful, targeted management actions PREPLANNED.

## Slide 262
Monitoring—Low Tech Display!
Accountability : Key to Energy Management
Notes: The white board shows the monthly average daily energy use for one section of the building, comparing 2006 to 2007, with the current month starred.
The table helps the staff “keep score” on energy performance—easy to see and use, easy to update. Without speeches or formal publication, whenever a staff member goes in and out of the work room, the numbers are in his face.
You can use sophisticated software and produce weather adjusted figures but if these values are locked away in a file and not visible to the staff who can make a difference, you’ve wasted the effort to produce the numbers in the first place.

## Slide 263
Benchmarking
Accountability : Key to Energy Management
Notes: Unusual buildings like convention centers are not in the ENERGY STAR database. This benchmarking table was developed by the facilities manager as part of his work applying for LEED EB certification.
He called colleagues in cities around the country in similar climate zone to obtain their energy use. This is an example of an informal benchmarking study, good enough to indicate that the Madison, WI facility is working relatively efficiently.
The only center with site EUI lower than Madison’s is Rochester--the Rochester center appears unusual, suggesting an all-electric building or incomplete data.
ENERGY NOTE: Jeff was able to analyze the energy use on days of conventions –the number of convention days over time has nearly doubled but the total energy use has remained about constant. (This is an example of normalizing energy use for activity, an important adjunct to normalizing for weather.)

## Slide 264: Accountability
Jeff—personally accountable to the facility manager for facility energy use
Engineering staff—accountable to Jeff for components of energy use
Entire staff maintains an energy-conscious culture
Weekly staff review of energy use
Accountability : Key to Energy Management
Notes: The Monona Terrace has integrated key aspects of energy management into their full management system.
If the building is not performing well in its energy use, the facility manager knows who to call: Jeff!
And Jeff knows who in his engineering staff is accountable for components of the facility’s energy use.

## Slide 265: Monona Terrace Evaluation
18 YES (including 5 Bonus items on monitoring)
2 NO
Accountability : Key to Energy Management
Notes: Jeff Griffith filled out the checklist for Monona Terrace on 22 Oct 2009. His evaluation: 18 YES 2 NO.
Item 7B Bonus was a no—they didn’t come up with a good way to predict the impact of the last upgrade
Item 10 NO: Jeff’s boss does not attend the weekly meeting but gets updates from Jeff in another session.

## Slide 266
Monona Terrace
LEED EB Gold Certification
  Significant energy savings
  Nontoxic cleaning products
  Use of clean energy
  High recycling rates
Accountability : Key to Energy Management
Notes: Monona Terrace qualified for LEED Existing Building Silver Level after the deployment and documentation of green practices in addition to their energy management.
Their energy management system used regular attention to achieve results, it was not a particularly “high tech” approach.
MORE ON LEED EB LEED Existing Building certification requires energy performance equivalent to high levels of ENERGY STAR ratings.
Here is the table that relates points for LEED to ENERGY STAR ratings:
ENERGY STAR Rating LEED Points (out of 30, Energy and Atmosphere Section)
71 or 21st Percentile Above National Median 1
73 or 23rd Percentile Above National Median 2
74 or 24th Percentile Above National Median 3
Then by 1 point/percentile until
83 or 33rd Percentile Above National Median 12
Then by 2 points/percentile
93 or 43rd Percentile Above National Median 17
95+ or 45th+ Percentile Above National Median 18

## Slide 267: Exercise 10: Plans for Next Week
Accountability : Key to Energy Management
Page 31
in the exercises
Notes: Instructor will describe the options for Exercise 14.
After 10 to 15 minutes, everyone directed to Exercise 14D for 2 minutes ,
If the room is set up, have them pair up and tell each other their plans (2 more minutes).
Then large group debrief (next slide)

## Slide 268
Poll: What Will You Do Next Week?
Collect 24 months of utility bills?
Use Portfolio Manager?
  Review EUI and rating
Test one discretionary action?
Go through energy management checklists?
Or something else?
Accountability : Key to Energy Management
Notes: This slide can be used as part of the debrief of the planning exercise.
Ask for show of hands to get the counts.
Ask someone who said they will collect utility data or use Portfolio Manager to say WHY they will do this and WHO they need to help.
Ask someone to describe their test of a discretionary action.
Anything Else?

## Slide 269: Recap and Send-off

## Slide 270
www.energystar.gov
This is the cycle we have used to guide our discussion.
It’s time to summarize.
Recap: The Management Content of Energy Management
Recap and Send-off

## Slide 271: Recap: Assess Performance
Don’t start with audits!
Recap and Send-off

## Slide 272: Recap: Assess Performance
Monitor
Know what performance actually is
Different time scales
  Year
  Month
  Day
  Hour or shorter
Benchmark
Know how performance compares
Relevant references
  Self reference (history)
  Similar buildings
  Local utility examples
  ENERGY STAR, etc.
Recap and Send-off

## Slide 273: Recap: Why Assess Performance?
To see striking patterns and big differences
Time-based performance
  Winter versus summer
  Weekday versus weekend
  Day versus night
One building versus other buildings’ performance
Predicted versus actual performance
Recap and Send-off

## Slide 274: Recap: Create Action Plan
Questions to guide you:
Where are there big differences?
What could cause the differences?
What can you adjust?
Ingredients of your plan:
Choose something to adjust
Monitor performance before and after
Identify limits and barriers
Repeat
Recap and Send-off

## Slide 275: Recap: Evaluate Progress
How?
Look at energy use over time
Do adjustments sync with improved energy use?
Why?
Prove that adjustments improve energy use
To guide your next actions
Recap and Send-off

## Slide 276: Recap: Accountability
Who is accountable to
Assess energy performance?
Create and carry out action plans to improve performance?
Evaluate progress?

## Slide 277: Recap: When are You Really Ready for Audits and Retrocommissioning?
When you have a monitoring and benchmarking system in place
When you have adjusted everything you can think of to improve energy performance
Notes: In the process of adjusting your setpoints and controls, you will have learned things that will make an audit and retro-commissioning more relevant and useful. You will have a foundation to judge the merits of proposed capital upgrades.

## Slide 278: And Now the Send-Off…
Recap and Send-off

## Slide 279
Re-cap and Send-Off
Energy Management is the Quickest, Cheapest, Cleanest Way to Extend World Energy Supplies
Energy management can provide nearly two times
the environmental impact of renewable energy!
Notes: If you pull the information in the previous slides together, we get to this conclusion:
Energy Management is the Quickest, Cheapest, Cleanest Way to Extend World Energy Supplies.
Comparing the savings with renewable energy, the most effective thing we can do is attack wasted energy and save.
We are not denigrating renewable energy but rather observing that we have tremendous potential in the buildings we have.
Energy management implies you will learn how to use energy more intelligently in your buildings, reducing waste and assuring that changes to procedures and equipment yield their potential.
The 14% national impact provides an achievable percentage of energy savings from work with existing buildings, derived from our estimate of 33% savings in building energy use—though there are diminishing returns as you tackle opportunities (the first 5% is usually less costly than the last 5%).
Another way to look at the same figures: if you make more effective use of energy derived from fossil fuel, the % of the energy pie contributed by renewables goes up, even if no more renewable production is added. Reducing the use of fossil fuels increases the relative impact of renewables.

## Slide 280: 33% Energy Savings Are Possible in Existing Buildings
Some from smarter use of what you have right now
Some from capital upgrades
Re-cap and Send-Off
Notes: The two ways to get the savings are managing what you have better (wringing out waste) and replacing equipment (HVAC systems, lighting, revised control systems, etc.)
This arithmetic applies to existing buildings, which is a huge opportunity. You hit design constraints and strong economic barriers beyond the level of 33%, with the current costs of energy and technology.
This seminar has focused on smarter use of the systems and technology you have right now, which can account for roughly half of the potential available savings. With your skills in monitoring and testing, you also increase the odds that your capital and retrocommissioning projects will achieve their potential.
We encourage you to begin to study your buildings with the tools we have introduced today so you can determine specific actions and start saving energy, dollars, and climate-changing greenhouse gas emissions.

## Slide 281
Sustained Energy Savings Require Management Actions
An individual must be accountable
Team-oriented atmosphere
Use of data to guide actions
Re-cap and Send-off
Notes: This slide reminds the audience that the necessary ingredients for sustained energy savings come from the organization of people and resources—management.
Management changes are critical to get the benefits from technical changes to O&M procedures, along with upgrades to new equipment . You will not get sustained energy savings without effective management of the kind we have presented today.

## Slide 282
Remember to Monitor!
Re-cap and Send-off
Notes: Our final word: Buildings are like small children: if you don’t watch them, they will wind up doing the strangest things!
So monitor performance—you have learned the basic elements of monitoring performance today and we expect to hear great things from you about your accomplishments!

## Slide 283: Supplementary Information
Resources for Your Energy Management Work

## Slide 284: References
Text and online references are listed in the References supplement

## Slide 285: Link to ASHRAE Bookstore
http://www.techstreet.com/ashrae
Check out the resources mentioned in this seminar and more at the online ASHRAE Bookstore!

## Slide 286
About the Seminar Leader
Richard J. Pearson, P.E.
ASHRAE Fellow and Distinguished Lecturer
Principal of Pearson Forensic Engineering, Madison, Wisconsin
dick@pearsonengineering.com / www.pearsonengineering.com
Principal Contributor—ASHRAE Publications
Procedures for Commercial Building Energy Audits, Second Edition (2011)
Energy Use and Management, Chapter 36, 2015 ASHRAE Handbook—HVAC Applications
Lead Instructor—University of Wisconsin College of Engineering
Department of Engineering Professional Development— Fundamentals Development—Fundamentals of Energy Auditing Course
Member of the National Register of Peer Professionals
Conducts Peer Reviews of GSA design projects for US courthouses, etc.

## Slide 287: About the Editor
Kevin Little, Ph.D. (statistics)
Principal, Informing Ecological Design LLC, Madison, Wisconsin
klittle@iecodesign.com www.iecodesign.com
Designer of information tools to foster better use of energy and other resources, including Energy Stewards™ web platform www.energystewards.net
Improvement Advisor with the Institute of Healthcare Improvement

## Slide 288: Evaluation and Certificate
ASHRAE values your comments about this course. You will receive your Certificate of Attendance when you finish the online course evaluation form at this URL: http://ali.ashrae.biz/2019annualconference/ Access code: t6v8 Be sure to add your appropriate license numbers.
Supplemental files for this course may be found at https://www.ashrae.org/June2019EnergyMgmt.
If you have any questions about ASHRAE Certificates, please contact Kelly Arnold, Administrative Assistant, at karnold@ashrae.org.
If you have any questions about ASHRAE courses, please contact Sarah Boyle, Managing Editor, at sboyle@ashrae.org.

## Slide 289: ASHRAE Career Enhancement Curriculum Program
Expand your knowledge of IAQ and Energy Savings Practices through a select series of ASHRAE Learning Institute courses
  Receive up-to-date instruction on new technology from industry experts
  Gain valuable HVAC knowledge
  Accelerate your career growth
  Receive a certificate for successful completion of the course series
Visit www.ashrae.org/careerpath to learn more.

## Slide 290: ASHRAE Professional Certification
Do you want to stand out from the crowd? Become ASHRAE certified. ASHRAE certification serves as a springboard for your continued professional development.
Assure employers and clients that you have mastered the body of knowledge that subject matter experts have identified as reflecting best practices.
Please visit the following URL to learn more about our programs: www.ashrae.org/certification
  Building Energy Assessment Professional
  Building Energy Modeling Professional
  Commissioning Process Management Professional
  Healthcare Facility Design Professional
  High-Performance Building Design Professional
  Operations & Performance Management Professional