## BPF Calculator
ASHRAE Standard 90.1-2025 Performance Rating Method (Appendix G) Building Performance Factor Calculation Tool
Published BPFs in Section 4 of ASHRAE Standard 90.1-2025 are based on nationally representative energy costs. Informative Appendix I describes a method allowing BPF's to be calculated based on site energy, source energy, or greenhouse gas emissions using representative national values for source energy and greenhouse gas emissions, shown below in the table labeled 2025 Published BPF Conversion Factors. By selecting the BPF Approach "As Published", in the table below, the published BPF values from ASHRAE 90.1-2025 Section 4.0 (energy cost) and Informative Appendix I (site energy, source energy and emissions) will be displayed. This calculator can be used to develop a custom set of Building Performance Factors (BPFs). These may be used with the Performance Rating Method of ASHRAE Standard 90.1-2025 when approved by the Rating Authority. Jurisdictions may chose to use this calculator to develop BPF values that better align with local metrics. Where a Jurisdiction requires the use of hourly or other time of use data to calculate energy costs, emissions or source energy, calculate and enter conversion factors representing an annual blended or annual average value. The methodology used by this calculator for calculating custom BPF values is described in ASHRAE 90.1-2025 Informative Appendix I.
Instructions for Developing Custom BPF Values 1. Select the BPF Approach "Custom BPF" in the table below. "As Published": This choice selects the published BPF values in ASHRAE Standard 90.1-2025 Standard ignoring any user entered metrics for electricity or natural gas. "Custom BPF": This choice allows users to create custom BPF values using custom metrics for cost, source energy or emissions.
2. After selecting "Custom BPF", enter user defined conversion factors for energy cost, emissions and/or source energy, for both electricity and natural gas, in the light red cells below. When using fossil fuels other than natural gas, enter values using the units as shown (1 therm = 10^5 BTU). The conversion factors used to calculate the 90.1-2025 Published BPF values for energy cost, source energy and GHG emisisons are shown in the table below.
Code Year: |  | 90.1-2025 |  |  |  |  | BPF Approach: | As Published
| Electricity | [12 empty] | Natural Gas (Fossil Fuel)
| Cost: | 0.1122 |  | $/site kWh |  |  |  | 0.032884 | $/site kBTU |  |  |  |  | Cost: | 0.838 |  | $/therm |  |  | 0.00838 | $/site kBtu
| Emissions: | 0.4709 |  | lb/site kWh |  |  |  | 0.13801 | lb/site kBTU |  |  |  |  | Emissions: | 14.7 |  | lb/therm |  |  | 0.147 | lb/site kBtu
| Source: | 8.27 |  | source kBtu/ site kWh |  |  |  | 2.4238 | source kBtu/ site kBTU |  |  |  |  | Source: | 123 |  | source kBtu/therm |  |  | 1.23 | source kBtu/site kBtu
| BPF_Cost | [20 empty] | 2025 Published BPF Conversion Factors
| Group | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| Apartment | 0.6083 | 0.56743 | 0.59832 | 0.57392 | 0.59221 | 0.56924 | 0.57886 | 0.57885 | 0.46088 | 0.55311 | 0.57348 | 0.5535 | 0.54236 | 0.5586 | 0.56822 | 0.52651 | 0.53479 | 0.53814 | 0.59497 |  | Elec Cost | 0.1122 | $/site kWh
| Medical | 0.59823 | 0.58599 | 0.58811 | 0.59528 | 0.59943 | 0.5974 | 0.58156 | 0.58667 | 0.55569 | 0.55993 | 0.57468 | 0.57715 | 0.57962 | 0.567 | 0.53344 | 0.57192 | 0.54623 | 0.55321 | 0.57092 |  | Elec Emissions | 0.471 | lb/site kWh
| Hotel | 0.58033 | 0.56469 | 0.57489 | 0.5583 | 0.55423 | 0.53513 | 0.53912 | 0.54386 | 0.5264 | 0.53094 | 0.52942 | 0.52225 | 0.52722 | 0.52795 | 0.52845 | 0.525 | 0.52947 | 0.5242 | 0.52732 |  | Elec Source | 8.27 | source kBtu/site kWh
| Office | 0.4281 | 0.41776 | 0.40319 | 0.40589 | 0.36917 | 0.38781 | 0.36819 | 0.38307 | 0.34978 | 0.35117 | 0.36692 | 0.36154 | 0.36544 | 0.36699 | 0.36635 | 0.3764 | 0.36438 | 0.36061 | 0.38731 |  | Gas Cost | 0.838 | $/therm
| Food.Svc | 0.57393 | 0.55238 | 0.55759 | 0.55008 | 0.54991 | 0.54669 | 0.58346 | 0.5561 | 0.54416 | 0.58999 | 0.56966 | 0.59528 | 0.62103 | 0.59074 | 0.6091 | 0.6284 | 0.6073 | 0.63908 | 0.67015 |  | Gas Emissions | 14.7 | lb/therm
| Retail | 0.41484 | 0.39994 | 0.37534 | 0.38789 | 0.33451 | 0.34277 | 0.33518 | 0.34124 | 0.34072 | 0.34604 | 0.36123 | 0.3686 | 0.36271 | 0.3647 | 0.38344 | 0.36644 | 0.36908 | 0.38485 | 0.41332 |  | Gas Source | 123 | source kBtu/therm
| School | 0.44524 | 0.44557 | 0.42915 | 0.43887 | 0.40866 | 0.42879 | 0.43019 | 0.39297 | 0.36814 | 0.36567 | 0.37759 | 0.37855 | 0.38311 | 0.38149 | 0.37797 | 0.38302 | 0.36853 | 0.38295 | 0.41404
| Warehouse | 0.23825 | 0.254 | 0.21326 | 0.23873 | 0.20128 | 0.21491 | 0.23806 | 0.20518 | 0.1764 | 0.23722 | 0.20811 | 0.21407 | 0.27681 | 0.23746 | 0.21522 | 0.31229 | 0.27669 | 0.28961 | 0.32447
| Other | 0.5268 | 0.5101 | 0.50096 | 0.50666 | 0.43812 | 0.4218 | 0.43039 | 0.42109 | 0.41751 | 0.43398 | 0.41879 | 0.44383 | 0.43581 | 0.42951 | 0.44784 | 0.44252 | 0.43837 | 0.44863 | 0.46925
| BPF_Source | [20 empty] | The BPF Calculator includes a special feature that compares 2 different tables of BPF values. Select the arrow to navigate to the BPF Compare Tool.
| Group | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| Apartment | 0.62 | 0.58 | 0.61 | 0.59 | 0.6 | 0.58 | 0.6 | 0.59 | 0.49 | 0.55 | 0.58 | 0.56 | 0.53 | 0.56 | 0.57 | 0.51 | 0.53 | 0.53 | 0.57
| Medical | 0.58 | 0.57 | 0.57 | 0.58 | 0.58 | 0.58 | 0.56 | 0.57 | 0.54 | 0.54 | 0.56 | 0.55 | 0.55 | 0.55 | 0.54 | 0.54 | 0.54 | 0.55 | 0.57
| Hotel | 0.59 | 0.57 | 0.59 | 0.57 | 0.57 | 0.55 | 0.56 | 0.56 | 0.55 | 0.55 | 0.55 | 0.55 | 0.54 | 0.55 | 0.55 | 0.53 | 0.55 | 0.54 | 0.54
| Office | 0.43 | 0.42 | 0.4 | 0.41 | 0.37 | 0.39 | 0.37 | 0.39 | 0.35 | 0.36 | 0.37 | 0.37 | 0.38 | 0.38 | 0.38 | 0.4 | 0.38 | 0.37 | 0.41
| Food.Svc | 0.58 | 0.56 | 0.57 | 0.56 | 0.56 | 0.56 | 0.6 | 0.59 | 0.57 | 0.64 | 0.62 | 0.65 | 0.68 | 0.64 | 0.67 | 0.69 | 0.67 | 0.7 | 0.73
| Retail | 0.41 | 0.4 | 0.38 | 0.39 | 0.33 | 0.34 | 0.34 | 0.35 | 0.34 | 0.36 | 0.37 | 0.39 | 0.38 | 0.39 | 0.41 | 0.39 | 0.39 | 0.42 | 0.45
| School | 0.45 | 0.45 | 0.43 | 0.44 | 0.41 | 0.43 | 0.43 | 0.4 | 0.38 | 0.36 | 0.39 | 0.4 | 0.38 | 0.4 | 0.4 | 0.38 | 0.37 | 0.39 | 0.43
| Warehouse | 0.24 | 0.25 | 0.21 | 0.24 | 0.2 | 0.21 | 0.24 | 0.21 | 0.18 | 0.29 | 0.23 | 0.25 | 0.36 | 0.29 | 0.25 | 0.4 | 0.34 | 0.36 | 0.4
| Other | 0.53 | 0.51 | 0.51 | 0.51 | 0.44 | 0.43 | 0.44 | 0.43 | 0.43 | 0.44 | 0.43 | 0.46 | 0.45 | 0.45 | 0.47 | 0.46 | 0.46 | 0.47 | 0.5
BPF_Emissions
| Group | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| Apartment | 0.63 | 0.59 | 0.63 | 0.61 | 0.63 | 0.61 | 0.62 | 0.62 | 0.54 | 0.55 | 0.6 | 0.57 | 0.52 | 0.56 | 0.58 | 0.5 | 0.52 | 0.51 | 0.56
| Medical | 0.54 | 0.53 | 0.53 | 0.54 | 0.54 | 0.54 | 0.53 | 0.55 | 0.51 | 0.5 | 0.52 | 0.51 | 0.5 | 0.51 | 0.55 | 0.5 | 0.53 | 0.55 | 0.57
| Hotel | 0.6 | 0.59 | 0.61 | 0.59 | 0.59 | 0.58 | 0.59 | 0.59 | 0.59 | 0.57 | 0.59 | 0.58 | 0.55 | 0.58 | 0.59 | 0.54 | 0.57 | 0.55 | 0.56
| Office | 0.43 | 0.42 | 0.4 | 0.41 | 0.37 | 0.39 | 0.37 | 0.39 | 0.35 | 0.37 | 0.38 | 0.4 | 0.4 | 0.4 | 0.41 | 0.43 | 0.41 | 0.39 | 0.43
| Food.Svc | 0.59 | 0.57 | 0.59 | 0.58 | 0.58 | 0.58 | 0.62 | 0.64 | 0.62 | 0.71 | 0.68 | 0.73 | 0.74 | 0.71 | 0.74 | 0.75 | 0.74 | 0.76 | 0.78
| Retail | 0.41 | 0.4 | 0.38 | 0.39 | 0.33 | 0.34 | 0.34 | 0.36 | 0.34 | 0.38 | 0.4 | 0.43 | 0.42 | 0.43 | 0.46 | 0.43 | 0.43 | 0.46 | 0.5
| School | 0.45 | 0.45 | 0.43 | 0.44 | 0.42 | 0.44 | 0.44 | 0.42 | 0.4 | 0.36 | 0.42 | 0.44 | 0.39 | 0.44 | 0.43 | 0.39 | 0.38 | 0.39 | 0.44
| Warehouse | 0.24 | 0.25 | 0.21 | 0.24 | 0.2 | 0.21 | 0.24 | 0.22 | 0.18 | 0.38 | 0.27 | 0.31 | 0.47 | 0.37 | 0.31 | 0.5 | 0.44 | 0.43 | 0.48
| Other | 0.54 | 0.52 | 0.52 | 0.52 | 0.45 | 0.43 | 0.45 | 0.46 | 0.46 | 0.46 | 0.46 | 0.5 | 0.48 | 0.49 | 0.51 | 0.48 | 0.48 | 0.49 | 0.53
BPF_Site
| Group | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| Apartment | 0.63 | 0.59 | 0.63 | 0.6 | 0.62 | 0.61 | 0.62 | 0.61 | 0.54 | 0.55 | 0.6 | 0.57 | 0.52 | 0.56 | 0.57 | 0.5 | 0.52 | 0.51 | 0.56
| Medical | 0.55 | 0.53 | 0.53 | 0.54 | 0.54 | 0.55 | 0.53 | 0.55 | 0.51 | 0.51 | 0.53 | 0.51 | 0.51 | 0.51 | 0.55 | 0.5 | 0.53 | 0.55 | 0.57
| Hotel | 0.6 | 0.59 | 0.6 | 0.59 | 0.59 | 0.58 | 0.58 | 0.59 | 0.58 | 0.56 | 0.58 | 0.58 | 0.54 | 0.57 | 0.59 | 0.54 | 0.57 | 0.55 | 0.55
| Office | 0.43 | 0.42 | 0.4 | 0.41 | 0.37 | 0.39 | 0.37 | 0.39 | 0.35 | 0.37 | 0.38 | 0.4 | 0.4 | 0.4 | 0.41 | 0.43 | 0.41 | 0.39 | 0.43
| Food.Svc | 0.59 | 0.57 | 0.58 | 0.58 | 0.58 | 0.58 | 0.62 | 0.64 | 0.62 | 0.71 | 0.68 | 0.72 | 0.74 | 0.71 | 0.74 | 0.74 | 0.73 | 0.76 | 0.78
| Retail | 0.41 | 0.4 | 0.38 | 0.39 | 0.33 | 0.34 | 0.34 | 0.36 | 0.34 | 0.38 | 0.4 | 0.43 | 0.42 | 0.42 | 0.45 | 0.43 | 0.43 | 0.46 | 0.5
| School | 0.45 | 0.45 | 0.43 | 0.44 | 0.42 | 0.44 | 0.44 | 0.42 | 0.39 | 0.36 | 0.41 | 0.44 | 0.39 | 0.44 | 0.43 | 0.39 | 0.38 | 0.39 | 0.44
| Warehouse | 0.24 | 0.25 | 0.21 | 0.24 | 0.2 | 0.21 | 0.24 | 0.22 | 0.18 | 0.37 | 0.27 | 0.31 | 0.46 | 0.36 | 0.31 | 0.49 | 0.43 | 0.43 | 0.47
| Other | 0.54 | 0.52 | 0.52 | 0.52 | 0.45 | 0.43 | 0.45 | 0.46 | 0.45 | 0.46 | 0.46 | 0.49 | 0.47 | 0.48 | 0.51 | 0.48 | 0.48 | 0.49 | 0.53
Goto BPF Compare

## Calculator (hidden)
[40 empty] | Code Year Options | Coefficent Tables |  |  | Code Year Options | Elec_Cost | Gas_Cost | Elec_Source | Gas_Source | Elec_Emissions | Gas_Emissions | BPF Approach
[40 empty] | 90.1-2025 | A_2025_v4 | B_2025_v4 | C_2025_v4 | 90.1-2025 | 0.1122 | 0.8381 | 8.27 | 123 | 0.471 | 14.7 | As Published
[8 empty] | Code Year | 90.1-2025_Pub | [30 empty] | 90.1-2025_Pub | A_2025_v4 | B_2025_v4 | C_2025_v4 | [7 empty] | _Pub | <<----DO NOT Delete formula
[8 empty] | Coeff Tables | [42 empty] | 1
Electricity
[8 empty] | Cost | 0.032884 | $/site kBtu
[8 empty] | Emissions | 0.13804 | lb/site kBtu
[8 empty] | Source | 2.4238 | source kBtu/site kBtu
Natural Gas
[8 empty] | Cost | 0.008381 | $/site kBtu
[8 empty] | Emissions | 0.147 | lb/site kBtu
[8 empty] | Source | 1.23 | source kBtu/site kBtu
Coefficient A | Proposed Gas/Proposed Electric | [18 empty] | BPF_Cost
Group | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8 | Group | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
Apartment | 0.28357 | 0.30283 | 0.38974 | 0.37292 | 0.47445 | 0.49059 | 0.62695 | 0.6343 | 1.0808 | 1.0421 | 0.7732 | 1.1797 | 1.348 | 0.97556 | 1.1857 | 1.546 | 1.3411 | 1.7461 | 2.1243 | Apartment | 0.6083 | 0.56743 | 0.59832 | 0.57392 | 0.59221 | 0.56924 | 0.57886 | 0.57885 | 0.46088 | 0.55311 | 0.57348 | 0.5535 | 0.54236 | 0.5586 | 0.56822 | 0.52651 | 0.53479 | 0.53814 | 0.59497
Medical | 0.030036 | 0.036766 | 0.041474 | 0.043474 | 0.049566 | 0.049362 | 0.075605 | 0.13329 | 0.14669 | 0.24557 | 0.15589 | 0.2539 | 0.32208 | 0.23911 | 0.59452 | 0.44451 | 0.57534 | 0.88938 | 1.1949 | Medical | 0.59823 | 0.58599 | 0.58811 | 0.59528 | 0.59943 | 0.5974 | 0.58156 | 0.58667 | 0.55569 | 0.55993 | 0.57468 | 0.57715 | 0.57962 | 0.567 | 0.53344 | 0.57192 | 0.54623 | 0.55321 | 0.57092
Hotel | 0.31414 | 0.33418 | 0.40361 | 0.39613 | 0.47521 | 0.53484 | 0.62056 | 0.71621 | 0.83928 | 0.99962 | 0.93068 | 1.1938 | 1.233 | 1.14 | 1.3145 | 1.4426 | 1.4359 | 1.8057 | 2.4081 | Hotel | 0.58033 | 0.56469 | 0.57489 | 0.5583 | 0.55423 | 0.53513 | 0.53912 | 0.54386 | 0.5264 | 0.53094 | 0.52942 | 0.52225 | 0.52722 | 0.52795 | 0.52845 | 0.525 | 0.52947 | 0.5242 | 0.52732
Office | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.072656 | 0.019186 | 0.34962 | 0.144 | 0.33135 | 0.56189 | 0.35106 | 0.38193 | 0.94226 | 0.67471 | 0.89358 | 1.4042 | Office | 0.4281 | 0.41776 | 0.40319 | 0.40589 | 0.36917 | 0.38781 | 0.36819 | 0.38307 | 0.34978 | 0.35117 | 0.36692 | 0.36154 | 0.36544 | 0.36699 | 0.36635 | 0.3764 | 0.36438 | 0.36061 | 0.38731
Food.Svc | 0.26591 | 0.28648 | 0.37619 | 0.35216 | 0.44351 | 0.48176 | 0.54918 | 0.88743 | 0.95215 | 1.9829 | 1.3565 | 2.0052 | 2.8684 | 1.9668 | 2.3745 | 3.6029 | 2.9744 | 4.6382 | 6.6051 | Food.Svc | 0.57393 | 0.55238 | 0.55759 | 0.55008 | 0.54991 | 0.54669 | 0.58346 | 0.5561 | 0.54416 | 0.58999 | 0.56966 | 0.59528 | 0.62103 | 0.59074 | 0.6091 | 0.6284 | 0.6073 | 0.63908 | 0.67015
Retail | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.078453 | 0.013392 | 0.42934 | 0.1971 | 0.42975 | 0.72714 | 0.45011 | 0.51507 | 1.0189 | 0.67845 | 1.2937 | 2.0003 | Retail | 0.41484 | 0.39994 | 0.37534 | 0.38789 | 0.33451 | 0.34277 | 0.33518 | 0.34124 | 0.34072 | 0.34604 | 0.36123 | 0.3686 | 0.36271 | 0.3647 | 0.38344 | 0.36644 | 0.36908 | 0.38485 | 0.41332
School | 0.035878 | 0.041033 | 0.051978 | 0.051556 | 0.063287 | 0.07482 | 0.082111 | 0.19929 | 0.19606 | 0.48245 | 0.37261 | 0.72728 | 0.79326 | 0.81029 | 0.77546 | 1.1304 | 0.96316 | 1.5022 | 2.6133 | School | 0.44524 | 0.44557 | 0.42915 | 0.43887 | 0.40866 | 0.42879 | 0.43019 | 0.39297 | 0.36814 | 0.36567 | 0.37759 | 0.37855 | 0.38311 | 0.38149 | 0.37797 | 0.38302 | 0.36853 | 0.38295 | 0.41404
Warehouse | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10244 | 0.0069165 | 2.3105 | 0.7017 | 1.1383 | 4.3148 | 1.9586 | 1.0915 | 5.7414 | 3.4051 | 5.4856 | 5.9258 | Warehouse | 0.23825 | 0.254 | 0.21326 | 0.23873 | 0.20128 | 0.21491 | 0.23806 | 0.20518 | 0.1764 | 0.23722 | 0.20811 | 0.21407 | 0.27681 | 0.23746 | 0.21522 | 0.31229 | 0.27669 | 0.28961 | 0.32447
Other | 0.16369 | 0.17557 | 0.21323 | 0.21328 | 0.17347 | 0.1516 | 0.19642 | 0.33453 | 0.43465 | 0.73094 | 0.4373 | 0.80405 | 1.0418 | 0.77874 | 0.81018 | 1.2946 | 1.0717 | 1.5463 | 2.318 | Other | 0.5268 | 0.5101 | 0.50096 | 0.50666 | 0.43812 | 0.4218 | 0.43039 | 0.42109 | 0.41751 | 0.43398 | 0.41879 | 0.44383 | 0.43581 | 0.42951 | 0.44784 | 0.44252 | 0.43837 | 0.44863 | 0.46925
Coefficient B | Baseline Electric/Proposed Electric | [18 empty] | BPF_Source
Group | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8 | Group | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
Apartment | 1.667 | 1.7961 | 1.7058 | 1.7821 | 1.7325 | 1.8107 | 1.7918 | 1.7818 | 2.3963 | 1.7965 | 1.7853 | 1.8507 | 1.7762 | 1.7882 | 1.7748 | 1.8192 | 1.8375 | 1.7777 | 1.5583 | Apartment | 0.62 | 0.58 | 0.61 | 0.59 | 0.6 | 0.58 | 0.6 | 0.59 | 0.49 | 0.55 | 0.58 | 0.56 | 0.53 | 0.56 | 0.57 | 0.51 | 0.53 | 0.53 | 0.57
Medical | 1.6152 | 1.6422 | 1.6355 | 1.6206 | 1.6075 | 1.6198 | 1.6585 | 1.6617 | 1.7391 | 1.7077 | 1.6777 | 1.6406 | 1.617 | 1.6874 | 1.91 | 1.6255 | 1.8099 | 1.8016 | 1.7569 | Medical | 0.58 | 0.57 | 0.57 | 0.58 | 0.58 | 0.58 | 0.56 | 0.57 | 0.54 | 0.54 | 0.56 | 0.55 | 0.55 | 0.55 | 0.54 | 0.54 | 0.54 | 0.55 | 0.57
Hotel | 1.752 | 1.8056 | 1.7784 | 1.8346 | 1.8583 | 1.9382 | 1.9339 | 1.9229 | 2.0154 | 1.9605 | 2.0053 | 2.0614 | 1.9437 | 2.005 | 2.0394 | 1.937 | 1.9965 | 1.9865 | 2.0038 | Hotel | 0.59 | 0.57 | 0.59 | 0.57 | 0.57 | 0.55 | 0.56 | 0.56 | 0.55 | 0.55 | 0.55 | 0.55 | 0.54 | 0.55 | 0.55 | 0.53 | 0.55 | 0.54 | 0.54
Office | 2.3359 | 2.3937 | 2.4802 | 2.4637 | 2.7088 | 2.5786 | 2.716 | 2.6366 | 2.8536 | 2.9153 | 2.767 | 2.8728 | 2.8524 | 2.8253 | 2.8686 | 2.8752 | 2.9213 | 2.903 | 2.8006 | Office | 0.43 | 0.42 | 0.4 | 0.41 | 0.37 | 0.39 | 0.37 | 0.39 | 0.35 | 0.36 | 0.37 | 0.37 | 0.38 | 0.38 | 0.38 | 0.4 | 0.38 | 0.37 | 0.41
Food.Svc | 1.7648 | 1.8394 | 1.8322 | 1.8562 | 1.8688 | 1.8854 | 1.7651 | 1.9427 | 1.9801 | 1.981 | 1.9805 | 1.9859 | 1.9498 | 1.9748 | 1.9724 | 1.9779 | 2.0291 | 2.0352 | 2.0405 | Food.Svc | 0.58 | 0.56 | 0.57 | 0.56 | 0.56 | 0.56 | 0.6 | 0.59 | 0.57 | 0.64 | 0.62 | 0.65 | 0.68 | 0.64 | 0.67 | 0.69 | 0.67 | 0.7 | 0.73
Retail | 2.4106 | 2.5004 | 2.6642 | 2.5781 | 2.9894 | 2.9174 | 2.9835 | 2.9808 | 2.9439 | 3.0175 | 2.8722 | 2.8973 | 2.9707 | 2.9333 | 2.8174 | 3.0104 | 2.915 | 2.9226 | 2.8386 | Retail | 0.41 | 0.4 | 0.38 | 0.39 | 0.33 | 0.34 | 0.34 | 0.35 | 0.34 | 0.36 | 0.37 | 0.39 | 0.38 | 0.39 | 0.41 | 0.39 | 0.39 | 0.42 | 0.45
School | 2.2519 | 2.2512 | 2.3404 | 2.2882 | 2.4619 | 2.3476 | 2.3422 | 2.6075 | 2.7886 | 2.704 | 2.7585 | 2.8592 | 2.6259 | 2.833 | 2.834 | 2.6226 | 2.7791 | 2.6416 | 2.5989 | School | 0.45 | 0.45 | 0.43 | 0.44 | 0.41 | 0.43 | 0.43 | 0.4 | 0.38 | 0.36 | 0.39 | 0.4 | 0.38 | 0.4 | 0.4 | 0.38 | 0.37 | 0.39 | 0.43
Warehouse | 4.1972 | 3.937 | 4.6891 | 4.1888 | 4.9682 | 4.6531 | 4.2006 | 4.9797 | 5.6777 | 5.9307 | 5.4379 | 5.6955 | 6.2078 | 5.6787 | 5.6453 | 5.8897 | 5.5309 | 5.8989 | 5.3333 | Warehouse | 0.24 | 0.25 | 0.21 | 0.24 | 0.2 | 0.21 | 0.24 | 0.21 | 0.18 | 0.29 | 0.23 | 0.25 | 0.36 | 0.29 | 0.25 | 0.4 | 0.34 | 0.36 | 0.4
Other | 1.9102 | 1.9753 | 2.0237 | 1.9958 | 2.3085 | 2.3964 | 2.3578 | 2.4563 | 2.4882 | 2.3831 | 2.4937 | 2.3945 | 2.4208 | 2.4839 | 2.3979 | 2.3818 | 2.4195 | 2.3855 | 2.3962 | Other | 0.53 | 0.51 | 0.51 | 0.51 | 0.44 | 0.43 | 0.44 | 0.43 | 0.43 | 0.44 | 0.43 | 0.46 | 0.45 | 0.45 | 0.47 | 0.46 | 0.46 | 0.47 | 0.5
Coefficient C | Baseline Gas/Proposed Electric | [18 empty] | BPF_Emissions
Apartment | 0.37557 | 0.40108 | 0.51634 | 0.49406 | 0.62872 | 0.65012 | 0.83098 | 0.88308 | 1.4564 | 1.929 | 1.1852 | 1.9587 | 2.7505 | 1.7543 | 2.0283 | 3.2505 | 2.6351 | 3.5608 | 4.051 | Group | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
Medical | 0.27152 | 0.31492 | 0.32488 | 0.30543 | 0.32116 | 0.29483 | 0.36958 | 0.39544 | 0.50115 | 0.74552 | 0.51606 | 0.80126 | 0.98056 | 0.72114 | 0.97588 | 1.2596 | 1.1349 | 1.6311 | 2.0721 | Apartment | 0.63 | 0.59 | 0.63 | 0.61 | 0.63 | 0.61 | 0.62 | 0.62 | 0.54 | 0.55 | 0.6 | 0.57 | 0.52 | 0.56 | 0.58 | 0.5 | 0.52 | 0.51 | 0.56
Hotel | 0.42829 | 0.45565 | 0.54922 | 0.53908 | 0.64574 | 0.72672 | 0.84085 | 0.98639 | 1.1406 | 1.5803 | 1.3011 | 1.7105 | 2.1544 | 1.7244 | 1.9103 | 2.6213 | 2.289 | 3.1353 | 4.1454 | Medical | 0.54 | 0.53 | 0.53 | 0.54 | 0.54 | 0.54 | 0.53 | 0.55 | 0.51 | 0.5 | 0.52 | 0.51 | 0.5 | 0.51 | 0.55 | 0.5 | 0.53 | 0.55 | 0.57
Office | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.087055 | 0.0759 | 0.73036 | 0.22919 | 0.49745 | 1.0826 | 0.56229 | 0.49744 | 1.646 | 1.1578 | 1.9683 | 2.7675 | Hotel | 0.6 | 0.59 | 0.61 | 0.59 | 0.59 | 0.58 | 0.59 | 0.59 | 0.59 | 0.57 | 0.59 | 0.58 | 0.55 | 0.58 | 0.59 | 0.54 | 0.57 | 0.55 | 0.56
Food.Svc | 0.37522 | 0.40445 | 0.52241 | 0.48981 | 0.60899 | 0.66073 | 0.74036 | 1.029 | 1.1909 | 2.2384 | 1.4982 | 2.1679 | 3.2866 | 2.2229 | 2.6009 | 4.2166 | 3.3972 | 5.4118 | 7.7048 | Office | 0.43 | 0.42 | 0.4 | 0.41 | 0.37 | 0.39 | 0.37 | 0.39 | 0.35 | 0.37 | 0.38 | 0.4 | 0.4 | 0.4 | 0.41 | 0.43 | 0.41 | 0.39 | 0.43
Retail | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032336 | 0.0042084 | 0.73975 | 0.13826 | 0.44285 | 1.1662 | 0.48361 | 0.52162 | 1.6763 | 1.0315 | 2.0895 | 3.1951 | Food.Svc | 0.59 | 0.57 | 0.59 | 0.58 | 0.58 | 0.58 | 0.62 | 0.64 | 0.62 | 0.71 | 0.68 | 0.73 | 0.74 | 0.71 | 0.74 | 0.75 | 0.74 | 0.76 | 0.78
School | 0.057256 | 0.065053 | 0.080853 | 0.079892 | 0.096605 | 0.11383 | 0.12173 | 0.26097 | 0.24943 | 1.4396 | 0.55476 | 1.0676 | 2.0092 | 1.2933 | 1.313 | 2.9048 | 2.3561 | 3.8037 | 5.5909 | Retail | 0.41 | 0.4 | 0.38 | 0.39 | 0.33 | 0.34 | 0.34 | 0.36 | 0.34 | 0.38 | 0.4 | 0.43 | 0.42 | 0.43 | 0.46 | 0.43 | 0.43 | 0.46 | 0.5
Warehouse | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083729 | 0.0041256 | 3.0105 | 0.88875 | 1.2994 | 5.4043 | 2.4897 | 1.1523 | 7.8397 | 4.7854 | 9.3437 | 9.4293 | School | 0.45 | 0.45 | 0.43 | 0.44 | 0.42 | 0.44 | 0.44 | 0.42 | 0.4 | 0.36 | 0.42 | 0.44 | 0.39 | 0.44 | 0.43 | 0.39 | 0.38 | 0.39 | 0.44
Other | 0.26399 | 0.2856 | 0.31763 | 0.3341 | 0.29362 | 0.25896 | 0.32152 | 0.47475 | 0.67587 | 1.3749 | 0.62907 | 1.2568 | 1.8954 | 1.2024 | 1.1616 | 2.4468 | 1.902 | 2.8329 | 3.8997 | Warehouse | 0.24 | 0.25 | 0.21 | 0.24 | 0.2 | 0.21 | 0.24 | 0.22 | 0.18 | 0.38 | 0.27 | 0.31 | 0.47 | 0.37 | 0.31 | 0.5 | 0.44 | 0.43 | 0.48
[20 empty] | Other | 0.54 | 0.52 | 0.52 | 0.52 | 0.45 | 0.43 | 0.45 | 0.46 | 0.46 | 0.46 | 0.46 | 0.5 | 0.48 | 0.49 | 0.51 | 0.48 | 0.48 | 0.49 | 0.53
BPF_Site
[20 empty] | Group | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
[20 empty] | Apartment | 0.63 | 0.59 | 0.63 | 0.6 | 0.62 | 0.61 | 0.62 | 0.61 | 0.54 | 0.55 | 0.6 | 0.57 | 0.52 | 0.56 | 0.57 | 0.5 | 0.52 | 0.51 | 0.56
[20 empty] | Medical | 0.55 | 0.53 | 0.53 | 0.54 | 0.54 | 0.55 | 0.53 | 0.55 | 0.51 | 0.51 | 0.53 | 0.51 | 0.51 | 0.51 | 0.55 | 0.5 | 0.53 | 0.55 | 0.57
[20 empty] | Hotel | 0.6 | 0.59 | 0.6 | 0.59 | 0.59 | 0.58 | 0.58 | 0.59 | 0.58 | 0.56 | 0.58 | 0.58 | 0.54 | 0.57 | 0.59 | 0.54 | 0.57 | 0.55 | 0.55
[20 empty] | Office | 0.43 | 0.42 | 0.4 | 0.41 | 0.37 | 0.39 | 0.37 | 0.39 | 0.35 | 0.37 | 0.38 | 0.4 | 0.4 | 0.4 | 0.41 | 0.43 | 0.41 | 0.39 | 0.43
[20 empty] | Food.Svc | 0.59 | 0.57 | 0.58 | 0.58 | 0.58 | 0.58 | 0.62 | 0.64 | 0.62 | 0.71 | 0.68 | 0.72 | 0.74 | 0.71 | 0.74 | 0.74 | 0.73 | 0.76 | 0.78
[20 empty] | Retail | 0.41 | 0.4 | 0.38 | 0.39 | 0.33 | 0.34 | 0.34 | 0.36 | 0.34 | 0.38 | 0.4 | 0.43 | 0.42 | 0.42 | 0.45 | 0.43 | 0.43 | 0.46 | 0.5
[20 empty] | School | 0.45 | 0.45 | 0.43 | 0.44 | 0.42 | 0.44 | 0.44 | 0.42 | 0.39 | 0.36 | 0.41 | 0.44 | 0.39 | 0.44 | 0.43 | 0.39 | 0.38 | 0.39 | 0.44
[20 empty] | Warehouse | 0.24 | 0.25 | 0.21 | 0.24 | 0.2 | 0.21 | 0.24 | 0.22 | 0.18 | 0.37 | 0.27 | 0.31 | 0.46 | 0.36 | 0.31 | 0.49 | 0.43 | 0.43 | 0.47
[20 empty] | Other | 0.54 | 0.52 | 0.52 | 0.52 | 0.45 | 0.43 | 0.45 | 0.46 | 0.45 | 0.46 | 0.46 | 0.49 | 0.47 | 0.48 | 0.51 | 0.48 | 0.48 | 0.49 | 0.53
BPFi,j=(EC+Ai,j *GC)/(Bi,j *EC+Ci,j *GC) (Equation X-1)
Ai,j, Bi,j, Ci,j = coefficients from Tables X5-2, X5-3 and X5-4 for building area type i and climate zone j
EC = custom electricity conversion factor expressed using the units shown in Table X5-1 for the selected metric
GC = custom natural gas conversion factor expressed using the units shown in Table X5-1 for the selected metric

## BPF Compare
|  | ASHRAE Standard 90.1-2025 Performance Rating Method (Appendix G) Building Performance Factor Comparison Tool | [22 empty] | Code Year Options | Elec_Cost | Gas_Cost | Elec_Source | Gas_Source | Elec_Emissions | Gas_Emissions | Elec_Site | Gas_Site | Do not delete
|  |  | Instructions for BPF Comparison Tool This worksheet can be used to compare 2 different sets of BPF Values. First, select the Approach and BPF metric type in the green cells (to the left) for the 2 cases you want to compare. Second, when selecting "Custom" as the Approach, enter user defined metrics for cost, source energy or emissions into the applicable Custom Metrics Table using the light red cells (to the right) . | [21 empty] | Custom1 | 0.1122 | 0.838 | 9.008 | 109 | 1.2 | 19.96 | 3.412 | 100 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
[25 empty] | Custom2 | 0.1122 | 0.838 | 8.27 | 123 | 0.471 | 14.7 | 3.412 | 100 | Do not delete 2: Do not delete
[25 empty] | 90.1-2025 | 0.1122 | 0.838 | 8.27 | 123 | 0.471 | 14.7 | 3.412 | 100 | bar: Do not delete 2
Code Year | 90.1-2025 | BPF_Cost | Table 1 | [30 empty] | Do not delete 2: 2
Approach | As Published |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8 | Custom Metrics Table 1 | [11 empty] | Do not delete 2: 3
Type | Cost | Apartment | 0.6083 | 0.56743 | 0.59832 | 0.57392 | 0.59221 | 0.56924 | 0.57886 | 0.57885 | 0.46088 | 0.55311 | 0.57348 | 0.5535 | 0.54236 | 0.5586 | 0.56822 | 0.52651 | 0.53479 | 0.53815 | 0.59497 | Elec Cost | 0.1122 | $/site kWh | [9 empty] | Do not delete 2: 4
Do Not Edit Cells Below |  | Medical | 0.59823 | 0.586 | 0.58811 | 0.59528 | 0.59943 | 0.5974 | 0.58156 | 0.58667 | 0.55569 | 0.55993 | 0.57468 | 0.57715 | 0.57963 | 0.567 | 0.53344 | 0.57193 | 0.54623 | 0.55321 | 0.57092 | Gas Cost | 0.838 | $/therm | [9 empty] | Do not delete 2: 5
Elec Metric | 0.032884 | Hotel | 0.58033 | 0.56469 | 0.57489 | 0.55829 | 0.55422 | 0.53513 | 0.53912 | 0.54386 | 0.52639 | 0.53094 | 0.52942 | 0.52224 | 0.52722 | 0.52795 | 0.52845 | 0.525 | 0.52947 | 0.5242 | 0.52732 | Elec Emissions | 1.2 | lb/site kWh | [9 empty] | Do not delete 2: 6
Gas Metric | 0.00838 | Office | 0.4281 | 0.41776 | 0.40319 | 0.40589 | 0.36917 | 0.38781 | 0.36819 | 0.38307 | 0.34978 | 0.35117 | 0.36692 | 0.36153 | 0.36544 | 0.36699 | 0.36635 | 0.3764 | 0.36437 | 0.36061 | 0.38731 | Gas Emissions | 19.96 | lb/therm | [9 empty] | Do not delete 2: 7
Coefficent A | A_2025_v4 | Food.Svc | 0.57392 | 0.55238 | 0.55759 | 0.55008 | 0.54991 | 0.54669 | 0.58346 | 0.55609 | 0.54416 | 0.58998 | 0.56966 | 0.59527 | 0.62102 | 0.59074 | 0.60909 | 0.62839 | 0.60729 | 0.63907 | 0.67014 | Elec Source | 9.008 | source kBtu/ site kWh | [9 empty] | Do not delete 2: 8
Coefficent B | B_2025_v4 | Retail | 0.41484 | 0.39994 | 0.37534 | 0.38789 | 0.33451 | 0.34277 | 0.33518 | 0.34124 | 0.34072 | 0.34604 | 0.36123 | 0.3686 | 0.36271 | 0.3647 | 0.38344 | 0.36643 | 0.36908 | 0.38484 | 0.41331 | Gas Source | 109 | kBtu/therm | [9 empty] | Do not delete 2: 9
Coefficent C | C_2025_v4 | School | 0.44524 | 0.44557 | 0.42915 | 0.43887 | 0.40866 | 0.42879 | 0.43019 | 0.39297 | 0.36813 | 0.36567 | 0.37759 | 0.37855 | 0.38311 | 0.38149 | 0.37797 | 0.38302 | 0.36853 | 0.38295 | 0.41404
|  | Warehouse | 0.23825 | 0.254 | 0.21326 | 0.23873 | 0.20128 | 0.21491 | 0.23806 | 0.20518 | 0.1764 | 0.23721 | 0.20811 | 0.21406 | 0.2768 | 0.23746 | 0.21522 | 0.31228 | 0.27668 | 0.2896 | 0.32446
|  | Other | 0.5268 | 0.5101 | 0.50096 | 0.50666 | 0.43812 | 0.4218 | 0.43039 | 0.42109 | 0.41751 | 0.43398 | 0.41878 | 0.44383 | 0.4358 | 0.42951 | 0.44784 | 0.44252 | 0.43837 | 0.44862 | 0.46924
Code Year | 90.1-2025 | BPF_Cost | Table 2
Approach | Custom |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8 | Custom Metrics Table 2
Type | Cost | Apartment | 0.6083 | 0.56743 | 0.59832 | 0.57392 | 0.59221 | 0.56924 | 0.57886 | 0.57885 | 0.46088 | 0.55311 | 0.57348 | 0.5535 | 0.54236 | 0.5586 | 0.56822 | 0.52651 | 0.53479 | 0.53815 | 0.59497 | Elec Cost | 0.1122 | $/site kWh
Do Not Edit Cells Below |  | Medical | 0.59823 | 0.586 | 0.58811 | 0.59528 | 0.59943 | 0.5974 | 0.58156 | 0.58667 | 0.55569 | 0.55993 | 0.57468 | 0.57715 | 0.57963 | 0.567 | 0.53344 | 0.57193 | 0.54623 | 0.55321 | 0.57092 | Gas Cost | 0.838 | $/therm
Elec Metric | 0.032884 | Hotel | 0.58033 | 0.56469 | 0.57489 | 0.55829 | 0.55422 | 0.53513 | 0.53912 | 0.54386 | 0.52639 | 0.53094 | 0.52942 | 0.52224 | 0.52722 | 0.52795 | 0.52845 | 0.525 | 0.52947 | 0.5242 | 0.52732 | Elec Emissions | 0.471 | lb/site kWh
Gas Metric | 0.00838 | Office | 0.4281 | 0.41776 | 0.40319 | 0.40589 | 0.36917 | 0.38781 | 0.36819 | 0.38307 | 0.34978 | 0.35117 | 0.36692 | 0.36153 | 0.36544 | 0.36699 | 0.36635 | 0.3764 | 0.36437 | 0.36061 | 0.38731 | Gas Emissions | 14.7 | lb/therm
Coefficent A | A_2025_v4 | Food.Svc | 0.57392 | 0.55238 | 0.55759 | 0.55008 | 0.54991 | 0.54669 | 0.58346 | 0.55609 | 0.54416 | 0.58998 | 0.56966 | 0.59527 | 0.62102 | 0.59074 | 0.60909 | 0.62839 | 0.60729 | 0.63907 | 0.67014 | Elec Source | 8.27 | source kBtu/ site kWh
Coefficent B | B_2025_v4 | Retail | 0.41484 | 0.39994 | 0.37534 | 0.38789 | 0.33451 | 0.34277 | 0.33518 | 0.34124 | 0.34072 | 0.34604 | 0.36123 | 0.3686 | 0.36271 | 0.3647 | 0.38344 | 0.36643 | 0.36908 | 0.38484 | 0.41331 | Gas Source | 123 | kBtu/therm
Coefficent C | C_2025_v4 | School | 0.44524 | 0.44557 | 0.42915 | 0.43887 | 0.40866 | 0.42879 | 0.43019 | 0.39297 | 0.36813 | 0.36567 | 0.37759 | 0.37855 | 0.38311 | 0.38149 | 0.37797 | 0.38302 | 0.36853 | 0.38295 | 0.41404
|  | Warehouse | 0.23825 | 0.254 | 0.21326 | 0.23873 | 0.20128 | 0.21491 | 0.23806 | 0.20518 | 0.1764 | 0.23721 | 0.20811 | 0.21406 | 0.2768 | 0.23746 | 0.21522 | 0.31228 | 0.27668 | 0.2896 | 0.32446
|  | Other | 0.5268 | 0.5101 | 0.50096 | 0.50666 | 0.43812 | 0.4218 | 0.43039 | 0.42109 | 0.41751 | 0.43398 | 0.41878 | 0.44383 | 0.4358 | 0.42951 | 0.44784 | 0.44252 | 0.43837 | 0.44862 | 0.46924
|  | Delta Comparison (Table 2 - Table 1) | [19 empty] | 2025 Published BPF Metrics (provided for reference)
|  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | Apartment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Elec Cost | 0.1122 | $/site kWh
|  | Medical | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas Cost | 0.838 | $/therm
|  | Hotel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Elec Emissions | 0.471 | lb/site kWh
|  | Office | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas Emissions | 14.7 | lb/therm
|  | Food.Svc | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Elec Source | 8.27 | source kBtu/ site kWh
|  | Retail | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas Source | 123 | kBtu/therm
|  | School | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Warehouse | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
% difference (delta to table 2)
|  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | Apartment | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Medical | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Hotel | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Office | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Food.Svc | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Retail | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | School | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Warehouse | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  | Other | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Go back to
BPF Calculator