## Introduction
Fan Power Limit Examples and Tool
version 1
2021-04-26
John Bade, 2050 Partners |  | johnbade@2050partners.com
Bryan Boyce, Energy Solutions |  | bboyce@energy-solution.com
The purpose of this workbook is to allow stakeholders to work with the proposed fan power limit updates for ASHRAE 90.1.
There are three worksheets that the user can work out of, one for each type of fan system (single fan, supply/return fan, or complex fan systems). In each worksheet the user can enter fan system parameters and see how the resulting power allowance for the proposal compares against the two existing options in 90.1-2019 (i.e., the motor nameplate method and the brake horsepower method). Users only need to modify the orange "input" cells.
Following the three template worksheets, there are a number of completed examples for a variety of fan system types and airflow levels. Stakeholders can easily view a side-by-side comparison for these worked examples. A summary table for these examples is also shown below.
Summary of Examples
No. | Fan System Type | Airflow Control | Airflow (cfm) | 90.1-2019 |  |  | Proposed | Percent Change between BHP method & proposed method
|  |  |  | Motor HP Method Result | BHP Method Result | BHP Method Result (est. input kW) | Proposed Result (kW)
1 | Single Fan, recirculating | MZ-VAV | 20000 | #REF! | #REF! | #REF! | #REF! | #REF!
2 | Single Fan, recirculating | MZ-VAV | 7500 | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Single Fan, recirculating | MZ-VAV | 4000 | #REF! | #REF! | #REF! | #REF! | #REF!
4 | Single Fan, recirculating | CAV | 20000 | #REF! | #REF! | #REF! | #REF! | #REF!
5 | Single Fan, recirculating | CAV | 7500 | #REF! | #REF! | #REF! | #REF! | #REF!
6 | Single Fan, recirculating | SZ-VAV | 20000 | #REF! | #REF! | #REF! | #REF! | #REF!
7 | Single Fan, recirculating | SZ-VAV | 7500 | #REF! | #REF! | #REF! | #REF! | #REF!
8 | ERV-recirculating | MZ-VAV | 8000 | #REF! | #REF! | #REF! | #REF! | #REF!
9 | ERV-recirculating | MZ-VAV | 7500 | #REF! | #REF! | #REF! | #REF! | #REF!
10 | Supply and Return | MZ-VAV | 20000 | #REF! | #REF! | #REF! | #REF! | #REF!
11 | Supply and Return | CAV | 20000 | #REF! | #REF! | #REF! | #REF! | #REF!

## Single Fan Template
|  |  |  | System Attributes |  |  |  |  | Key:
| Description: |  |  |  | Single fan, recirculating |  |  |  | Input
| CAV/SZ-VAV/MZ-VAV: |  |  |  | MZ-VAV |  |  |  | Calculation
| Calculation Method: |  |  |  | Single-cabinet fan |  |  |  | Hard-coded value
[5 empty] | Supply |  |  |  | Output
| Variable Speed Drive (Yes/No) |  |  |  | Yes
| Transmission (Direct/V-belt): |  |  |  | Direct
| Airflow (cfm): |  |  |  | 30000
|  |  |  | MERV 8 Filter: | Yes
|  |  |  | MERV 9-12 Filter: | No
|  |  |  | MERV 13+ Filter: | Yes
|  |  |  | S3. Cooling or Heat Pump Coil: | Yes
|  |  |  | S4. Heating Coil: | No
|  |  |  | S4. Gas Furnace: | Yes
|  |  |  | S4. Electric Resistance Heat: | No
|  |  |  | S6. Energy Recovery Ventilator: | No
|  |  |  | S5. Economizer Return Damper | Yes
|  |  |  | S7. Hot Gas Reheat Coil | No
|  |  |  | S8. 50% Turndown (Single-Zone VAV only) | No
Results of Fan Power Limit Based on Method:
|  |  |  | 90.1-2019 Methods: |  |  |  |  | Proposed Method:
| Motor Nameplate Method, max hp |  |  |  | 45
| Resulting maximum standard motor size, hp |  |  |  | 40
| Brake Horsepower Method |  |  |  | Airflow (cfm) | Additional Pressure Loss (in. wc) | Allowed Brake Horsepower |  | Calculation per the proposed Fan Power Limits: | Airflow | Allowed w/cfm | Fan Power Allowance (kW)
| Base Allowance: |  |  |  | 30000 | N/A | 39 |  | S1. Supply Base Allowance: | 30000 | 0.48004 | 14.4013
| MERV 9-12 Filter: |  |  |  | 0 | 0.5 | 0 |  | S2. Up to MERV 12 Filter: | 30000 | 0.073261 | 2.1978 | [8 empty] | Multi-Zone VAV System airflow (cfm) |  |  | Constant Volume/Single-zone VAV airflow (cfm)
| MERV 13 or greater filter: |  |  |  | 30000 | 0.9 | 6.5359 |  | S2. MERV 13 to 16 Filter: | 30000 | 0.16545 | 4.9635 | [6 empty] | Air System Component | >10,000 | >5,000 and ≤10,000 | ≤5,000 | >10,000 | >5,000 and ≤10,000 | ≤5,000
| Energy Recovery Supply Airstream: |  |  |  | 0 | 0.875 | 0 |  | S2. MERV 13-16 Filter Downstream of Cooling Coil: | 0 | 0.18401 | 0
| Energy Recovery Exhaust Airstream: |  |  |  | 0 | 0.875 | 0 |  | S3. Cooling or Heat Pump Coil: | 30000 | 0.11003 | 3.3008 | [6 empty] | Supply System Base Allowance for air handler serving floor ≤6 floors away. | 0.48004 | 0.47247 | 0.41298 | 0.2483 | 0.26699 | 0.24303
| Deduction for no Central Cooling Device: |  |  |  | 0 | -0.6 | 0 |  | S4. Heating Coil: | 0 | 0.054919 | 0 | [6 empty] | Filter MERV 12 or less | 0.073261 | 0.079265 | 0.093947 | 0.075395 | 0.083644 | 0.097212
| Deduction for no Central Heating Device: |  |  |  | 0 | -0.3 | 0 |  | S4. Gas Furnace: | 30000 | 0.073261 | 2.1978 | [6 empty] | MERV 13 to MERV 16 Filter (mid-life) | 0.16545 | 0.17663 | 0.20986 | 0.16767 | 0.18544 | 0.21706
| Deduction for Electric Resistance Heat: |  |  |  | 0 | -0.2 | 0 |  | S4. Electric Resistance Heat: | 0 | 0.036599 | 0 | [6 empty] | MERV 13 to MERV 16 Final filter located downstream of thermal conditioning equipment. (mid-life) | 0.18401 | 0.19591 | 0.23285 | 0.186 | 0.20548 | 0.24052
| TOTAL: | [5 empty] | 45.5359 |  | S5. Economizer Return Damper: | 30000 | 0.036599 | 1.098 | [6 empty] | Hydronic/DX cooling coil, or heat pump coil (wet) [Healthcare facilities can select twice] | 0.11003 | 0.11842 | 0.14051 | 0.11248 | 0.1247 | 0.14582
[9 empty] | S6. Energy Recovery (ERR=62.5%) | 0 | 0.15063 | 0 | [6 empty] | Hydronic heating coil (central) | 0.054919 | 0.0497 | 0.047113 | 0.056722 | 0.05253 | 0.048606
[9 empty] | S7. Hot Gas Reheat Coil: | 0 | 0.036599 | 0 | [6 empty] | Gas heat | 0.073261 | 0.059576 | 0.070564 | 0.075395 | 0.062934 | 0.060758
[9 empty] | S8. 50% Turndown Single-Zone VAV: | 0 | 0 | 0 | [6 empty] | Electric heat | 0.036599 | 0.039804 | 0.047113 | 0.037943 | 0.042094 | 0.048606
[11 empty] | supply side power allowance (kW) | 28.1592 | [6 empty] | Economizer return damper | 0.036599 | 0.039804 | 0.047113 | 0.037943 | 0.042094 | 0.048606
[5 empty] | Supply Fan | [13 empty] | Enthalpy Recovery Ratio ≥ 0.60 and <0.65) | 0.15063 | 0.16116 | 0.19142 | 0.15299 | 0.16933 | 0.19825
| Upsize Motor? |  |  |  | No |  |  |  | ER1. Exhaust/Return/Relief Base Allowance: | 30000 | 0.2483 | 7.449 | [6 empty] | Reheat coil for dehumidification | 0.036599 | 0.039804 | 0.047113 | 0.037943 | 0.042094 | 0.048606
| Assumed Motor Nameplate Size: |  |  |  | 50 |  |  |  | ER2. Filter, any MERV value, in the return airstream: | 0 | 0.037943 | 0 | [6 empty] | Low-turndown single-zone VAV fan systems meeting the requirements in note 4. | 0 | 0 | 0 | 0.093977 | 0.10423 | 0.072909
| Brake horsepower: |  |  |  | 45.5359 |  |  |  | ER3. Energy Recovery (ERR=62.5%): | 0 | 0.15299 | 0
| ODP/TEFC |  |  |  | ODP | [5 empty] | return/exhaust side power allowance | 7.449
| Number of Poles |  |  |  | 4 | [13 empty] | Exhaust System Base Allowance | 0.2483 | 0.25638 | 0.23088 | 0.19995 | 0.19187 | 0.19442
| Wire-to-Shaft effciency per AMCA 207: |  |  |  | 91.7% |  |  |  | Proposed Method Total Supply and Exhaust/Return (kW): |  |  | 35.6082 | [6 empty] | Filter (any MERV value) | 0.037943 | 0.042237 | 0.048606 | 0.038769 | 0.043165 | 0.048606
| Fan electical power (kW): |  |  |  | 37.0309 |  |  |  | Estimated allowance per current requirements (kW): |  |  | 37.0309 | [6 empty] | Enthalpy Recovery Ratio ≥ 0.60 and <0.65) | 0.15299 | 0.16985 | 0.19862 | 0.15529 | 0.17319 | 0.19928
| Watts per cfm (W): |  |  |  | 1.2344 |  |  |  | Reduction from estimated current allowance: |  |  | 3.842%
|  | Motor Efficiency Calculations | [13 empty] | Lookups
|  |  |  | ηR | [8 empty] | Voltage | Motor Type | Tansmission | M Poles | Qty | Qty M/F | Num MP | VFD current or HP | FEI Pressure Basis | System Type | Yes/No |  | MERV Value
|  |  |  | ODP |  |  |  | TEFC |  |  |  |  | 460 | ODP | Direct | 2 | 0 | 1 | 2 | HP | Static | CAV | No |  | MERV 8 or less
|  |  | Fan System 1 | 2 POLE | 4 POLE | 6 POLE | 8 POLE | 2 POLE | 4 POLE | 6 POLE | 8 POLE |  | 230 | TEFC | V-Belt | 4 | 1 | 1.5 | 4 | Current (A) | Total | SZ-VAV | Yes |  | MERV 9-12
|  |  |  | 0.93 | 0.945 | 0.941 | 0.924 | 0.93 | 0.945 | 0.941 | 0.91 |  | 575 |  | Synchronous Belt | 6 | 2 | 2 | 6 |  |  | MZ-VAV |  |  | MERV 13-16
|  | Quantity of Motors | 1 | [9 empty] | 208 |  | Coupling | 8 | 3 | 3 | 8 | [5 empty] | MERV 13-16 Downstream
|  | Motor Namplate Horsepower | 50 | ODP 2 POLE: Motor Factors; ODP 4 POLE: 2 POLE; ODP 8 POLE: 4 POLE; TEFC 4 POLE: 6 & 8 POLE | [5 empty] | 4 | 5
|  | Brake HP of 1 fan at design airflow | 45.5359 | [13 empty] | 5 | 7.5 | bar: ODP 4 POLE to TEFC 6 POLE
|  | ODP or TEFC | ODP | With VFD | 1.0226 | 0.00485 | 1.0218 | 0.0037 | 1.0211 | 0.00384 | [6 empty] | 6 | 10
|  |  |  | DOL | 1.0621 | 0.02769 | 1.0461 | 0.01621 | 1.047 | 0.01732 | [6 empty] | 7 | 15
|  | Number of Motor Poles | 4 | [13 empty] | 8 | 20
|  | Transmission | Direct | ODP 4 POLE: VFD Factors | [5 empty] | 9 | 25
|  | Quantity of VFD's | 1 | ODP 4 POLE: HP; ODP 6 POLE: d; ODP 8 POLE: e; TEFC 2 POLE: f | [5 empty] | 10 | 30
|  | Size of VFD's | 50 | Below | 50 | 0.9879 | 0.0184 | -0.0017 | [8 empty] | 11 | 40
|  |  |  | Above | 60 | 0.9719 | 0.0145 | 0.0118 | [8 empty] | 12 | 50
|  |  |  | Linear interpol. | 0 | 0.9879 | 0.0184 | -0.0017 | [8 empty] | 13 | 60
[17 empty] | 14 | 75
[17 empty] | 15 | 100
BHP | Belt Efficiency ηb | Motor Shaft Power (HP) Hm | ηR | Lm | a | b | c | Motor Efficiency ηm | Lc | VFD effiiciency ηc | VFD & Motor Efficiency ηmc | Power Consumption kW | VFD, Motor & Transmission Efficiency ηsystem |  |  |  | 16 | 125
45.5359 | 1 | 45.5359 | 0.945 | 0.91072 | 1.0218 | 0.0037 | -0.018083 | 94.76% | 0.96111 | 96.77% | 91.7% | 37.0309 | 91.7% |  |  |  | 17 | 150
[17 empty] | 18 | 200
[17 empty] | 19 | 250
[17 empty] | 20 | 300
[17 empty] | 21 | 350
[17 empty] | 22 | 400
[17 empty] | 23 | 450
[17 empty] | 24 | 500
25
26
37
38
39
40

## Sup-Ret Fan Template
[5 empty] | System Attributes |  |  |  | Key:
|  | Description: |  |  |  | Supply and Return Fan |  |  | Input
|  | CAV/SZ-VAV/MZ-VAV: |  |  |  | CAV |  |  | Calculation
|  | Calculation Method: |  |  |  | Single-Cabinet Fan System |  |  | Hard-coded value
[6 empty] | Supply | Exhaust/Return |  | Output
|  | Variable Speed Drive (Yes/No) |  |  |  | Yes | Yes
|  | Transmission (Direct/V-belt): |  |  |  | V-Belt | V-Belt
|  | Airflow (cfm): |  |  |  | 7000 | 7000
|  | Est return/exhaust/relief fan fraction of total bhp |  |  |  | 35%
Airflow
[6 empty] | Supply | Return/Exhaust
|  |  | S2. Filter: | MERV 13-16 |  | 7000
|  |  | S3. Cooling or Heat Pump Coil: | Yes |  | 7000
|  |  | S4. Heating Coil: | No |  | 0
|  |  | S4. Gas Furnace: | Yes |  | 7000
|  |  | S4. Electric Resistance Heat: | No |  | 0
|  |  | S6 and ER3. Energy Recovery Ventilator: |  |  | 0 | 0
|  |  | S5. Economizer Return Damper |  |  | 7000
|  |  | S7. Hot Gas Reheat Coil | No |  | 0
|  |  | S8. 50% Turndown (Single-Zone VAV only) | No |  | 0
|  |  | ER2. Filter, any MERV value, in the return airstream |  |  |  | 0
Note: Grey cells contain airflow values that are automatically populated but can be overridden if necessary. Orange cells must be populated by the user.
Results of Fan Power Limit Based on Method:
| 90.1-2019 Methods: | [7 empty] | Proposed Method:
| Motor Nameplate Method, max hp |  |  |  | 7.7
| Resulting maximum standard motor size, hp |  |  |  | 7.5
| Brake Horsepower Method |  |  |  | Airflow (cfm) | Additional Pressure Loss (in. wc) | Allowed Brake Horsepower |  | Calculation per the proposed Fan Power Limits | Airflow | Allowed w/cfm | Fan Power Allowance (kW)
| Base Allowance: |  |  |  | 7000 | N/A | 6.58 |  | S1. Supply Base Allowance: | 7000 | 0.26699 | 1.869
| MERV 9-12 Filter: |  |  |  | 0 | 0.5 | 0 |  | S2. Up to MERV 12 Filter: | 0 | 0.083644 | 0 | [8 empty] | Multi-Zone VAV System airflow (cfm) |  |  | Constant Volume/Single-zone VAV airflow (cfm)
| MERV 13 or greater filter: |  |  |  | 7000 | 0.9 | 1.5251 |  | S2. MERV 13 to 16 Filter: | 7000 | 0.18544 | 1.298 | [6 empty] | Air System Component | >10,000 | >5,000 and ≤10,000 | ≤5,000 | >10,000 | >5,000 and ≤10,000 | ≤5,000
| Energy Recovery Supply Airstream: |  |  |  | 0 | 0.875 | 0 |  | S2. MERV 13-16 Filter Downstream of Cooling Coil: | 0 | 0.20548 | 0
| Energy Recovery Exhaust Airstream: |  |  |  | 0 | 0.875 | 0 |  | S3. Cooling or Heat Pump Coil: | 7000 | 0.1247 | 0.87288 | [6 empty] | Supply System Base Allowance for air handler serving floor ≤6 floors away. | 0.48004 | 0.47247 | 0.41298 | 0.2483 | 0.26699 | 0.24303
| Deduction for no Central Cooling Device: |  |  |  | 0 | -0.6 | 0 |  | S4. Heating Coil: | 0 | 0.05253 | 0 | [6 empty] | Filter MERV 12 or less | 0.073261 | 0.079265 | 0.093947 | 0.075395 | 0.083644 | 0.097212
| Deduction for no Central Heating Device: |  |  |  | 0 | -0.3 | 0 |  | S4. Gas Furnace: | 7000 | 0.062934 | 0.44054 | [6 empty] | MERV 13 to MERV 16 Filter (mid-life) | 0.16545 | 0.17663 | 0.20986 | 0.16767 | 0.18544 | 0.21706
| Deduction for Electric Resistance Heat: |  |  |  | 0 | -0.2 | 0 |  | S4. Electric Resistance Heat: | 0 | 0.042094 | 0 | [6 empty] | MERV 13 to MERV 16 Final filter located downstream of thermal conditioning equipment. (mid-life) | 0.18401 | 0.19591 | 0.23285 | 0.186 | 0.20548 | 0.24052
| TOTAL: | [5 empty] | 8.1051 |  | S5. Economizer Return Damper: | 7000 | 0.042094 | 0.29466 | [6 empty] | Hydronic/DX cooling coil, or heat pump coil (wet) [Healthcare facilities can select twice] | 0.11003 | 0.11842 | 0.14051 | 0.11248 | 0.1247 | 0.14582
[9 empty] | S6. Energy Recovery (ERR=62.5%) | 0 | 0.16933 | 0 | [6 empty] | Hydronic heating coil (central) | 0.054919 | 0.0497 | 0.047113 | 0.056722 | 0.05253 | 0.048606
[9 empty] | S7. Hot Gas Reheat Coil: | 0 | 0.042094 | 0 | [6 empty] | Gas heat | 0.073261 | 0.059576 | 0.070564 | 0.075395 | 0.062934 | 0.060758
[5 empty] | Supply Fan | Exhaust/ Return/ Relief Fan |  |  | S8. 50% Turndown Single-Zone VAV: | 0 | 0.10423 | 0 | [6 empty] | Electric heat | 0.036599 | 0.039804 | 0.047113 | 0.037943 | 0.042094 | 0.048606
[11 empty] | supply side power allowance (kW) | 4.7751 | [6 empty] | Economizer return damper | 0.036599 | 0.039804 | 0.047113 | 0.037943 | 0.042094 | 0.048606
[19 empty] | Enthalpy Recovery Ratio ≥ 0.60 and <0.65) | 0.15063 | 0.16116 | 0.19142 | 0.15299 | 0.16933 | 0.19825
| Upsize Motor? |  |  |  | Yes | Yes |  |  | ER1. Exhaust/Return/Relief Base Allowance: | 7000 | 0.19187 | 1.3431 | [6 empty] | Reheat coil for dehumidification | 0.036599 | 0.039804 | 0.047113 | 0.037943 | 0.042094 | 0.048606
| Assumed Motor Nameplate Size: |  |  |  | 10 | 5 |  |  | ER2. Filter, any MERV value, in the return airstream: | 0 | 0.043165 | 0 | [6 empty] | Low-turndown single-zone VAV fan systems meeting the requirements in note 4. | 0 | 0 | 0 | 0.093977 | 0.10423 | 0.072909
| Brake horsepower: |  |  |  | 5.2683 | 2.8368 |  |  | ER3. Energy Recovery (ERR=62.5%): | 0 | 0.17319 | 0 |  | 9.3213
| ODP/TEFC |  |  |  | TEFC | TEFC |  |  |  |  | return/exhaust side power allowance (kW) | 1.3431 |  | 1.0253
| Number of Poles |  |  |  | 4 | 4 | [7 empty] | 0.25633 |  |  |  |  | Exhaust System Base Allowance | 0.2483 | 0.25638 | 0.23088 | 0.19995 | 0.19187 | 0.19442
| Wire-to-Shaft effciency per AMCA 207: |  |  |  | 82.36% | 78.67% |  |  | Proposed Method Total Supply and Exhaust/Return (kW): |  |  | 6.1182 |  | 1117.6179 |  |  |  |  | Filter (any MERV value) | 0.037943 | 0.042237 | 0.048606 | 0.038769 | 0.043165 | 0.048606
| Fan electical power (kW): |  |  |  | 4.7703 | 2.6891 |  |  | Estimated allowance per current requirements (kW): |  |  | 7.4593 |  | 13411.4145 |  |  |  |  | Enthalpy Recovery Ratio ≥ 0.60 and <0.65) | 0.15299 | 0.16985 | 0.19862 | 0.15529 | 0.17319 | 0.19928
| Watts per cfm (W): |  |  |  | 0.68146 | 0.38416 |  |  | Reduction from estimated current allowance: |  |  | 17.98%
8.2046
7.2119
|  | Motor Efficiency Calculations | [13 empty] | Lookups
|  |  |  | ηR | [8 empty] | Voltage | Motor Type | Tansmission | M Poles | Qty | Qty M/F | Num MP | VFD current or HP | FEI Pressure Basis | System Type | Yes/No |  | MERV Value
|  |  |  | ODP |  |  |  | TEFC |  |  |  |  | 460 | ODP | Direct | 2 | 0 | 1 | 2 | HP | Static | CAV | No |  | MERV 8 or less
|  |  | Fan System 1 | 2 POLE | 4 POLE | 6 POLE | 8 POLE | 2 POLE | 4 POLE | 6 POLE | 8 POLE |  | 230 | TEFC | V-Belt | 4 | 1 | 1.5 | 4 | Current (A) | Total | SZ-VAV | Yes |  | MERV 9-12
|  |  |  | 0.895 | 0.917 | 0.917 | 0.902 | 0.902 | 0.917 | 0.91 | 0.875 |  | 575 |  | Synchronous Belt | 6 | 2 | 2 | 6 |  |  | MZ-VAV | Yes - twice |  | MERV 13-16
|  | Quantity of Motors | 1 | [9 empty] | 208 |  | Coupling | 8 | 3 | 3 | 8 | [5 empty] | MERV 13-16 Downstream
|  | Motor Namplate Horsepower | 10 | ODP 2 POLE: Motor Factors; ODP 4 POLE: 2 POLE; ODP 8 POLE: 4 POLE; TEFC 4 POLE: 6 & 8 POLE | [5 empty] | 4 | 5
|  | Brake HP of 1 fan at design airflow | 5.2683 | [13 empty] | 5 | 7.5 | bar: ODP 4 POLE to TEFC 6 POLE
|  | ODP or TEFC | TEFC | With VFD | 1.0334 | 0.00808 | 1.0387 | 0.01296 | 1.0402 | 0.01572 | [6 empty] | 6 | 10
|  |  |  | DOL | 1.0853 | 0.03783 | 1.0794 | 0.03481 | 1.0811 | 0.03846 | [6 empty] | 7 | 15
|  | Number of Motor Poles | 4 | [13 empty] | 8 | 20
|  | Transmission | V-Belt | ODP 4 POLE: VFD Factors | [5 empty] | 9 | 25
|  | Quantity of VFD's | 1 | ODP 4 POLE: HP; ODP 6 POLE: d; ODP 8 POLE: e; TEFC 2 POLE: f | [5 empty] | 10 | 30
|  | Size of VFD's | 10 | Below | 10 | 0.9787 | 0.0222 | 0.0019 | [8 empty] | 11 | 40
|  |  |  | Above | 15 | 0.98185 | 0.01985 | 0.0007 | [8 empty] | 12 | 50
|  |  |  | Linear interpol. | 0 | 0.9787 | 0.0222 | 0.0019 | [8 empty] | 13 | 60
[17 empty] | 14 | 75
[17 empty] | 15 | 100
BHP | Belt Efficiency ηb | Motor Shaft Power (HP) Hm | ηR | Lm | a | b | c | Motor Efficiency ηm | Lc | VFD effiiciency ηc | VFD & Motor Efficiency ηmc | Power Consumption kW | VFD, Motor & Transmission Efficiency ηsystem |  |  |  | 16 | 125
5.2683 | 0.9434 | 5.5844 | 0.917 | 0.55844 | 1.0387 | 0.01296 | -0.025371 | 92.36% | 0.60464 | 94.52% | 87.3% | 4.7703 | 82.36% |  |  |  | 17 | 150
[17 empty] | 18 | 200
[17 empty] | 19 | 250
[17 empty] | 20 | 300 | bar: ODP 2 POLE
|  |  |  | ODP 2 POLE: ODP; TEFC 2 POLE: TEFC | [5 empty] | 21 | 350
|  |  | Fan System 2 | 2 POLE | 4 POLE | 6 POLE | 8 POLE | 2 POLE | 4 POLE | 6 POLE | 8 POLE | [5 empty] | 22 | 400
|  |  |  | 0.865 | 0.895 | 0.895 | 0.885 | 0.885 | 0.895 | 0.895 | 0.84 | [5 empty] | 23 | 450
|  | Quantity of Motors | 1 | [13 empty] | 24 | 500
|  | Motor Namplate Horsepower | 5 | ODP 2 POLE: Motor Factors; ODP 4 POLE: 2 POLE; ODP 8 POLE: 4 POLE; TEFC 4 POLE: 6 & 8 POLE | [5 empty] | 25
|  | Brake HP of 1 fan at design airflow | 2.8368 | [13 empty] | 26 | bar: ODP 4 POLE to TEFC 6 POLE
|  | ODP or TEFC | TEFC | With VFD | 1.0364 | 0.00975 | 1.0429 | 0.01596 | 1.0446 | 0.02024 | [6 empty] | 37
|  |  |  | DOL | 1.0924 | 0.04197 | 1.0875 | 0.04009 | 1.0905 | 0.04588 | [6 empty] | 38
|  | Number of Motor Poles | 4 | [13 empty] | 39
|  | Transmission | V-Belt | ODP 4 POLE: VFD Factors | [5 empty] | 40
|  | Quantity of VFD's | 1 | ODP 4 POLE: HP; ODP 6 POLE: d; ODP 8 POLE: e; TEFC 2 POLE: f
|  | Size of VFD's | 5 | Below | 5 | 0.9775 | 0.0284 | -0.0027
|  |  |  | Above | 7.5 | 0.9781 | 0.0253 | -0.0004
|  |  |  | Linear interpol. | 0 | 0.9775 | 0.0284 | -0.0027
BHP | Belt Efficiency ηb | Motor Shaft Power (HP) Hm | ηR | Lm | a | b | c | Motor Efficiency ηm | Lc | VFD effiiciency ηc | VFD & Motor Efficiency ηmc | Power Consumption kW | VFD, Motor & Transmission Efficiency ηsystem
2.8368 | 0.93283 | 3.041 | 0.895 | 0.6082 | 1.0429 | 0.01596 | -0.026497 | 90.07% | 0.67523 | 93.62% | 84.33% | 2.6891 | 78.67%

## Complex System Template
[6 empty] | System Attributes |  |  |  | Key:
|  |  | Description: |  |  |  | Single fan, recirculating |  |  | Input
|  |  | CAV/SZ-VAV/MZ-VAV: |  |  |  | MZ-VAV |  |  | Calculation
|  |  | Calculation Method: |  |  |  | Complex Fan System |  |  | Hard-coded value
[7 empty] | Supply | Exhaust/Return |  | Output
|  |  | Variable Speed Drive (Yes/No) |  |  |  | Yes | Yes
|  |  | Transmission (Direct/V-belt): |  |  |  | Direct | Direct
|  |  | Airflow (cfm): |  |  |  | 8000 | 7600
|  |  | Est return/exhaust/relief fan fraction of total bhp |  |  |  | 20%
Airflow
[7 empty] | Supply | Return/Exhaust
|  |  |  | S2. Filter: | MERV 13-16 Downstream |  | 3000
|  |  |  | S3. Cooling or Heat Pump Coil: | Yes |  | 8000
|  |  |  | S4. Heating Coil: | No |  | 0
|  |  |  | S4. Gas Furnace: | Yes |  | 8000
|  |  |  | S4. Electric Resistance Heat: | No |  | 0
|  |  |  | S6 and ER3. Energy Recovery Ventilator: |  |  | 3000 | 2600
|  |  |  | S5. Economizer Return Damper |  |  | 5000
|  |  |  | S7. Hot Gas Reheat Coil | No |  | 0
|  |  |  | S8. 50% Turndown (Single-Zone VAV only) | No |  | 0
|  |  |  | ER2. Filter, any MERV value, in the return airstream |  |  |  | 7600
Note: Grey cells contain airflow values that are automatically populated but can be overridden if necessary. Orange cells must be populated by the user.
Results of Fan Power Limit Based on Method:
| 90.1-2019 Methods: | [7 empty] | Proposed Method:
| Motor Nameplate Method, max hp |  |  |  | 12
| Resulting maximum standard motor size, hp |  |  |  | 10
| Brake Horsepower Method |  |  |  | Airflow (cfm) | Additional Pressure Loss (in. wc) | Allowed Brake Horsepower |  | Calculation per the proposed Fan Power Limits |  |  |  |  | Airflow | Allowed w/cfm | Fan Power Allowance (kW)
| Base Allowance: |  |  |  | 8000 | N/A | 10.4 |  | S1. Supply Base Allowance: |  |  |  |  | 8000 | 0.47247 | 3.7798
| MERV 9-12 Filter: |  |  |  | 0 | 0.5 | 0 |  | S2. Up to MERV 12 Filter: |  |  |  |  | 0 | 0.079265 | 0 | [8 empty] | Multi-Zone VAV System airflow (cfm) |  |  | Constant Volume/Single-zone VAV airflow (cfm)
| MERV 13 or greater filter: |  |  |  | 3000 | 0.9 | 0.65359 |  | S2. MERV 13 to 16 Filter: |  |  |  |  | 0 | 0.17663 | 0 | [6 empty] | Air System Component | >10,000 | >5,000 and ≤10,000 | ≤5,000 | >10,000 | >5,000 and ≤10,000 | ≤5,000
| Energy Recovery Supply Airstream: |  |  |  | 3000 | 0.875 | 0.63544 |  | S2. MERV 13-16 Filter Downstream of Cooling Coil: |  |  |  |  | 3000 | 0.19591 | 0.58772
| Energy Recovery Exhaust Airstream: |  |  |  | 2600 | 0.875 | 0.55071 |  | S3. Cooling or Heat Pump Coil: |  |  |  |  | 8000 | 0.11842 | 0.94733 | [6 empty] | Supply System Base Allowance for air handler serving floor ≤6 floors away. | 0.48004 | 0.47247 | 0.41298 | 0.2483 | 0.26699 | 0.24303
| Deduction for no Central Cooling Device: |  |  |  | 0 | -0.6 | 0 |  | S4. Heating Coil: |  |  |  |  | 0 | 0.0497 | 0 | [6 empty] | Filter MERV 12 or less | 0.073261 | 0.079265 | 0.093947 | 0.075395 | 0.083644 | 0.097212
| Deduction for no Central Heating Device: |  |  |  | 0 | -0.3 | 0 |  | S4. Gas Furnace: |  |  |  |  | 8000 | 0.059576 | 0.47661 | [6 empty] | MERV 13 to MERV 16 Filter (mid-life) | 0.16545 | 0.17663 | 0.20986 | 0.16767 | 0.18544 | 0.21706
| Deduction for Electric Resistance Heat: |  |  |  | 0 | -0.2 | 0 |  | S4. Electric Resistance Heat: |  |  |  |  | 0 | 0.039804 | 0 | [6 empty] | MERV 13 to MERV 16 Final filter located downstream of thermal conditioning equipment. (mid-life) | 0.18401 | 0.19591 | 0.23285 | 0.186 | 0.20548 | 0.24052
| TOTAL: | [5 empty] | 12.2397 |  | S5. Economizer Return Damper: |  |  |  |  | 5000 | 0.039804 | 0.19902 | [6 empty] | Hydronic/DX cooling coil, or heat pump coil (wet) [Healthcare facilities can select twice] | 0.11003 | 0.11842 | 0.14051 | 0.11248 | 0.1247 | 0.14582
[9 empty] | S6. Energy Recovery (ERR=62.5%) |  |  |  |  | 3000 | 0.16116 | 0.48348 | [6 empty] | Hydronic heating coil (central) | 0.054919 | 0.0497 | 0.047113 | 0.056722 | 0.05253 | 0.048606
[9 empty] | S7. Hot Gas Reheat Coil: |  |  |  |  | 0 | 0.039804 | 0 | [6 empty] | Gas heat | 0.073261 | 0.059576 | 0.070564 | 0.075395 | 0.062934 | 0.060758
[5 empty] | Supply Fan | Exhaust/ Return/ Relief Fan |  |  | S8. 50% Turndown Single-Zone VAV: |  |  |  |  | 0 | 0 | 0 | [6 empty] | Electric heat | 0.036599 | 0.039804 | 0.047113 | 0.037943 | 0.042094 | 0.048606
| Motor Calculations: | [13 empty] | supply side power allowance (kW) | 6.4739 | [6 empty] | Economizer return damper | 0.036599 | 0.039804 | 0.047113 | 0.037943 | 0.042094 | 0.048606
[23 empty] | Enthalpy Recovery Ratio ≥ 0.60 and <0.65) | 0.15063 | 0.16116 | 0.19142 | 0.15299 | 0.16933 | 0.19825
| Upsize Motor? |  |  |  | Yes | No |  |  | ER1. Exhaust/Return/Relief Base Allowance: |  |  |  |  | 7600 | 0.25638 | 1.9485 | [6 empty] | Reheat coil for dehumidification | 0.036599 | 0.039804 | 0.047113 | 0.037943 | 0.042094 | 0.048606
| Assumed Motor Nameplate Size: |  |  |  | 15 | 3 |  |  | ER2. Filter, any MERV value, in the return airstream: |  |  |  |  | 7600 | 0.042237 | 0.321 | [6 empty] | Low-turndown single-zone VAV fan systems meeting the requirements in note 4. | 0 | 0 | 0 | 0.093977 | 0.10423 | 0.072909
| Brake horsepower: |  |  |  | 9.7918 | 2.4479 |  |  | ER3. Energy Recovery (ERR=62.5%): |  |  |  |  | 2600 | 0.16985 | 0.4416
| ODP/TEFC |  |  |  | ODP | ODP | [8 empty] | return/exhaust side power allowance (kW) | 2.7111
| Number of Poles |  |  |  | 4 | 4 | [16 empty] | Exhaust System Base Allowance | 0.2483 | 0.25638 | 0.23088 | 0.19995 | 0.19187 | 0.19442
| Wire-to-Shaft effciency per AMCA 207: |  |  |  | 89.59% | 81.4% |  |  | Proposed Method Total Supply and Exhaust/Return (kW): | [6 empty] | 9.185 | [6 empty] | Filter (any MERV value) | 0.037943 | 0.042237 | 0.048606 | 0.038769 | 0.043165 | 0.048606
| Fan electical power (kW): |  |  |  | 8.1506 | 2.2426 |  |  | Estimated allowance per current requirements (kW): | [6 empty] | 10.3932 | [6 empty] | Enthalpy Recovery Ratio ≥ 0.60 and <0.65) | 0.15299 | 0.16985 | 0.19862 | 0.15529 | 0.17319 | 0.19928
| Watts per cfm (W): |  |  |  | 1.0188 | 0.29508 |  |  | Reduction from estimated current allowance: | [6 empty] | 11.62%
|  | Motor Efficiency Calculations | [17 empty] | Lookups
|  |  |  | ηR | [8 empty] | Voltage | Motor Type | Tansmission | M Poles | Qty | Qty M/F | Num MP | VFD current or HP | FEI Pressure Basis | System Type | Yes/No | MERV Value
|  |  |  | ODP |  |  |  | TEFC |  |  |  |  | 460 | ODP | Direct | 2 | 0 | 1 | 2 | HP | Static | CAV | No | MERV 8 or less
|  |  | Fan System 1 | 2 POLE | 4 POLE | 6 POLE | 8 POLE | 2 POLE | 4 POLE | 6 POLE | 8 POLE |  | 230 | TEFC | V-Belt | 4 | 1 | 1.5 | 4 | Current (A) | Total | SZ-VAV | Yes | MERV 9-12
|  |  |  | 0.902 | 0.93 | 0.917 | 0.902 | 0.91 | 0.924 | 0.917 | 0.875 |  | 575 |  | Synchronous Belt | 6 | 2 | 2 | 6 |  |  | MZ-VAV | Yes - twice | MERV 13-16
|  | Quantity of Motors | 1 | [9 empty] | 208 |  | Coupling | 8 | 3 | 3 | 8 |  |  |  |  | MERV 13-16 Downstream
|  | Motor Namplate Horsepower | 15 | ODP 2 POLE: Motor Factors; ODP 4 POLE: 2 POLE; ODP 8 POLE: 4 POLE; TEFC 4 POLE: 6 & 8 POLE | [5 empty] | 4 | 5
|  | Brake HP of 1 fan at design airflow | 9.7918 | [13 empty] | 5 | 7.5 | bar: ODP 4 POLE to TEFC 6 POLE
|  | ODP or TEFC | ODP | With VFD | 1.0304 | 0.00641 | 1.0344 | 0.00996 | 1.0359 | 0.01121 | [6 empty] | 6 | 10
|  |  |  | DOL | 1.0781 | 0.03368 | 1.0713 | 0.02953 | 1.0716 | 0.03104 | [6 empty] | 7 | 15
|  | Number of Motor Poles | 4 | [13 empty] | 8 | 20
|  | Transmission | Direct | ODP 4 POLE: VFD Factors | [5 empty] | 9 | 25
|  | Quantity of VFD's | 1 | ODP 4 POLE: HP; ODP 6 POLE: d; ODP 8 POLE: e; TEFC 2 POLE: f | [5 empty] | 10 | 30
|  | Size of VFD's | 15 | Below | 15 | 0.98185 | 0.01985 | 0.0007 | [8 empty] | 11 | 40
|  |  |  | Above | 20 | 0.985 | 0.0175 | -0.0005 | [8 empty] | 12 | 50
|  |  |  | Linear interpol. | 0 | 0.98185 | 0.01985 | 0.0007 | [8 empty] | 13 | 60
[17 empty] | 14 | 75
[17 empty] | 15 | 100
BHP | Belt Efficiency ηb | Motor Shaft Power (HP) Hm | ηR | Lm | a | b | c | Motor Efficiency ηm | Lc | VFD effiiciency ηc | VFD & Motor Efficiency ηmc | Power Consumption kW | VFD, Motor & Transmission Efficiency ηsystem |  |  |  | 16 | 125
9.7918 | 1 | 9.7918 | 0.93 | 0.65279 | 1.0344 | 0.00996 | -0.024229 | 93.8% | 0.69596 | 95.51% | 89.59% | 8.1506 | 89.59% |  |  |  | 17 | 150
[17 empty] | 18 | 200
[17 empty] | 19 | 250
[17 empty] | 20 | 300 | bar: ODP 2 POLE
|  |  |  | ODP 2 POLE: ODP; TEFC 2 POLE: TEFC | [5 empty] | 21 | 350
|  |  | Fan System 2 | 2 POLE | 4 POLE | 6 POLE | 8 POLE | 2 POLE | 4 POLE | 6 POLE | 8 POLE | [5 empty] | 22 | 400
|  |  |  | 0.855 | 0.869 | 0.885 | 0.875 | 0.865 | 0.895 | 0.895 | 0.825 | [5 empty] | 23 | 450
|  | Quantity of Motors | 1 | [13 empty] | 24 | 500
|  | Motor Namplate Horsepower | 3 | ODP 2 POLE: Motor Factors; ODP 4 POLE: 2 POLE; ODP 8 POLE: 4 POLE; TEFC 4 POLE: 6 & 8 POLE | [5 empty] | 25
|  | Brake HP of 1 fan at design airflow | 2.4479 | [13 empty] | 26 | bar: ODP 4 POLE to TEFC 6 POLE
|  | ODP or TEFC | ODP | With VFD | 1.0327 | 0.01338 | 1.0402 | 0.02467 | 1.0676 | 0.0424 | [6 empty] | 37
|  |  |  | DOL | 1.1135 | 0.06436 | 1.1064 | 0.06571 | 1.1296 | 0.08027 | [6 empty] | 38
|  | Number of Motor Poles | 4 | [13 empty] | 39
|  | Transmission | Direct | ODP 4 POLE: VFD Factors | [5 empty] | 40
|  | Quantity of VFD's | 1 | ODP 4 POLE: HP; ODP 6 POLE: d; ODP 8 POLE: e; TEFC 2 POLE: f
|  | Size of VFD's | 3 | Below | 3 | 0.9789 | 0.0342 | -0.0079
|  |  |  | Above | 5 | 0.9775 | 0.0284 | -0.0027
|  |  |  | Linear interpol. | 0 | 0.9789 | 0.0342 | -0.0079
BHP | Belt Efficiency ηb | Motor Shaft Power (HP) Hm | ηR | Lm | a | b | c | Motor Efficiency ηm | Lc | VFD effiiciency ηc | VFD & Motor Efficiency ηmc | Power Consumption kW | VFD, Motor & Transmission Efficiency ηsystem
2.4479 | 1 | 2.4479 | 0.869 | 0.81598 | 1.0402 | 0.02467 | -0.015117 | 86.86% | 0.9394 | 93.71% | 81.4% | 2.2426 | 81.4%

## Complex System Template (2)
[6 empty] | System Attributes |  |  |  | Key:
|  |  | Description: |  |  |  | Single fan, recirculating |  |  | Input
|  |  | CAV/SZ-VAV/MZ-VAV: |  |  |  | MZ-VAV |  |  | Calculation
|  |  | Calculation Method: |  |  |  | Complex Fan System |  |  | Hard-coded value
[7 empty] | Supply | Exhaust/Return |  | Output
|  |  | Variable Speed Drive (Yes/No) |  |  |  | Yes | Yes
|  |  | Transmission (Direct/V-belt): |  |  |  | Direct | Direct
|  |  | Airflow (cfm): |  |  |  | 8000 | 7600
|  |  | Est return/exhaust/relief fan fraction of total bhp |  |  |  | 20%
Airflow
[7 empty] | Supply | Return/Exhaust
|  |  |  | S2. Filter: | MERV 13-16 |  | 3000
|  |  |  | S3. Cooling or Heat Pump Coil: | Yes |  | 8000
|  |  |  | S4. Heating Coil: | No |  | 0
|  |  |  | S4. Gas Furnace: | Yes |  | 8000
|  |  |  | S4. Electric Resistance Heat: | No |  | 0
|  |  |  | S6 and ER3. Energy Recovery Ventilator: |  |  | 3000 | 2600
|  |  |  | S5. Economizer Return Damper |  |  | 5000
|  |  |  | S7. Hot Gas Reheat Coil | No |  | 0
|  |  |  | S8. 50% Turndown (Single-Zone VAV only) | No |  | 0
|  |  |  | ER2. Filter, any MERV value, in the return airstream |  |  |  | 7600
Note: Grey cells contain airflow values that are automatically populated but can be overridden if necessary. Orange cells must be populated by the user.
Results of Fan Power Limit Based on Method:
| 90.1-2019 Methods: | [7 empty] | Proposed Method:
| Motor Nameplate Method, max hp |  |  |  | 12
| Resulting maximum standard motor size, hp |  |  |  | 10
| Brake Horsepower Method |  |  |  | Airflow (cfm) | Additional Pressure Loss (in. wc) | Allowed Brake Horsepower |  | Calculation per the proposed Fan Power Limits |  |  |  |  | Airflow | Allowed w/cfm | Fan Power Allowance (kW)
| Base Allowance: |  |  |  | 8000 | N/A | 10.4 |  | S1. Supply Base Allowance: |  |  |  |  | 8000 | 0.47247 | 3.7798
| MERV 9-12 Filter: |  |  |  | 0 | 0.5 | 0 |  | S2. Up to MERV 12 Filter: |  |  |  |  | 0 | 0.079265 | 0 | [8 empty] | Multi-Zone VAV System airflow (cfm) |  |  | Constant Volume/Single-zone VAV airflow (cfm)
| MERV 13 or greater filter: |  |  |  | 3000 | 0.9 | 0.65359 |  | S2. MERV 13 to 16 Filter: |  |  |  |  | 3000 | 0.17663 | 0.52988 | [6 empty] | Air System Component | >10,000 | >5,000 and ≤10,000 | ≤5,000 | >10,000 | >5,000 and ≤10,000 | ≤5,000
| Energy Recovery Supply Airstream: |  |  |  | 3000 | 0.875 | 0.63544 |  | S2. MERV 13-16 Filter Downstream of Cooling Coil: |  |  |  |  | 0 | 0.19591 | 0
| Energy Recovery Exhaust Airstream: |  |  |  | 2600 | 0.875 | 0.55071 |  | S3. Cooling or Heat Pump Coil: |  |  |  |  | 8000 | 0.11842 | 0.94733 | [6 empty] | Supply System Base Allowance for air handler serving floor ≤6 floors away. | 0.48004 | 0.47247 | 0.41298 | 0.2483 | 0.26699 | 0.24303
| Deduction for no Central Cooling Device: |  |  |  | 0 | -0.6 | 0 |  | S4. Heating Coil: |  |  |  |  | 0 | 0.0497 | 0 | [6 empty] | Filter MERV 12 or less | 0.073261 | 0.079265 | 0.093947 | 0.075395 | 0.083644 | 0.097212
| Deduction for no Central Heating Device: |  |  |  | 0 | -0.3 | 0 |  | S4. Gas Furnace: |  |  |  |  | 8000 | 0.059576 | 0.47661 | [6 empty] | MERV 13 to MERV 16 Filter (mid-life) | 0.16545 | 0.17663 | 0.20986 | 0.16767 | 0.18544 | 0.21706
| Deduction for Electric Resistance Heat: |  |  |  | 0 | -0.2 | 0 |  | S4. Electric Resistance Heat: |  |  |  |  | 0 | 0.039804 | 0 | [6 empty] | MERV 13 to MERV 16 Final filter located downstream of thermal conditioning equipment. (mid-life) | 0.18401 | 0.19591 | 0.23285 | 0.186 | 0.20548 | 0.24052
| TOTAL: | [5 empty] | 12.2397 |  | S5. Economizer Return Damper: |  |  |  |  | 5000 | 0.039804 | 0.19902 | [6 empty] | Hydronic/DX cooling coil, or heat pump coil (wet) [Healthcare facilities can select twice] | 0.11003 | 0.11842 | 0.14051 | 0.11248 | 0.1247 | 0.14582
[9 empty] | S6. Energy Recovery (ERR=62.5%) |  |  |  |  | 3000 | 0.16116 | 0.48348 | [6 empty] | Hydronic heating coil (central) | 0.054919 | 0.0497 | 0.047113 | 0.056722 | 0.05253 | 0.048606
[9 empty] | S7. Hot Gas Reheat Coil: |  |  |  |  | 0 | 0.039804 | 0 | [6 empty] | Gas heat | 0.073261 | 0.059576 | 0.070564 | 0.075395 | 0.062934 | 0.060758
[5 empty] | Supply Fan | Exhaust/ Return/ Relief Fan |  |  | S8. 50% Turndown Single-Zone VAV: |  |  |  |  | 0 | 0 | 0 | [6 empty] | Electric heat | 0.036599 | 0.039804 | 0.047113 | 0.037943 | 0.042094 | 0.048606
| Motor Calculations: | [13 empty] | supply side power allowance (kW) | 6.4161 | [6 empty] | Economizer return damper | 0.036599 | 0.039804 | 0.047113 | 0.037943 | 0.042094 | 0.048606
[23 empty] | Enthalpy Recovery Ratio ≥ 0.60 and <0.65) | 0.15063 | 0.16116 | 0.19142 | 0.15299 | 0.16933 | 0.19825
| Upsize Motor? |  |  |  | Yes | No |  |  | ER1. Exhaust/Return/Relief Base Allowance: |  |  |  |  | 7600 | 0.25638 | 1.9485 | [6 empty] | Reheat coil for dehumidification | 0.036599 | 0.039804 | 0.047113 | 0.037943 | 0.042094 | 0.048606
| Assumed Motor Nameplate Size: |  |  |  | 15 | 3 |  |  | ER2. Filter, any MERV value, in the return airstream: |  |  |  |  | 7600 | 0.042237 | 0.321 | [6 empty] | Low-turndown single-zone VAV fan systems meeting the requirements in note 4. | 0 | 0 | 0 | 0.093977 | 0.10423 | 0.072909
| Brake horsepower: |  |  |  | 9.7918 | 2.4479 |  |  | ER3. Energy Recovery (ERR=62.5%): |  |  |  |  | 2600 | 0.16985 | 0.4416
| ODP/TEFC |  |  |  | ODP | ODP | [8 empty] | return/exhaust side power allowance (kW) | 2.7111
| Number of Poles |  |  |  | 4 | 4 | [16 empty] | Exhaust System Base Allowance | 0.2483 | 0.25638 | 0.23088 | 0.19995 | 0.19187 | 0.19442
| Wire-to-Shaft effciency per AMCA 207: |  |  |  | 89.59% | 81.4% |  |  | Proposed Method Total Supply and Exhaust/Return (kW): | [6 empty] | 9.1272 | [6 empty] | Filter (any MERV value) | 0.037943 | 0.042237 | 0.048606 | 0.038769 | 0.043165 | 0.048606
| Fan electical power (kW): |  |  |  | 8.1506 | 2.2426 |  |  | Estimated allowance per current requirements (kW): | [6 empty] | 10.3932 | [6 empty] | Enthalpy Recovery Ratio ≥ 0.60 and <0.65) | 0.15299 | 0.16985 | 0.19862 | 0.15529 | 0.17319 | 0.19928
| Watts per cfm (W): |  |  |  | 1.0188 | 0.29508 |  |  | Reduction from estimated current allowance: | [6 empty] | 12.18%
|  | Motor Efficiency Calculations | [17 empty] | Lookups
|  |  |  | ηR | [8 empty] | Voltage | Motor Type | Tansmission | M Poles | Qty | Qty M/F | Num MP | VFD current or HP | FEI Pressure Basis | System Type | Yes/No | MERV Value
|  |  |  | ODP |  |  |  | TEFC |  |  |  |  | 460 | ODP | Direct | 2 | 0 | 1 | 2 | HP | Static | CAV | No | MERV 8 or less
|  |  | Fan System 1 | 2 POLE | 4 POLE | 6 POLE | 8 POLE | 2 POLE | 4 POLE | 6 POLE | 8 POLE |  | 230 | TEFC | V-Belt | 4 | 1 | 1.5 | 4 | Current (A) | Total | SZ-VAV | Yes | MERV 9-12
|  |  |  | 0.902 | 0.93 | 0.917 | 0.902 | 0.91 | 0.924 | 0.917 | 0.875 |  | 575 |  | Synchronous Belt | 6 | 2 | 2 | 6 |  |  | MZ-VAV | Yes - twice | MERV 13-16
|  | Quantity of Motors | 1 | [9 empty] | 208 |  | Coupling | 8 | 3 | 3 | 8 |  |  |  |  | MERV 13-16 Downstream
|  | Motor Namplate Horsepower | 15 | ODP 2 POLE: Motor Factors; ODP 4 POLE: 2 POLE; ODP 8 POLE: 4 POLE; TEFC 4 POLE: 6 & 8 POLE | [5 empty] | 4 | 5
|  | Brake HP of 1 fan at design airflow | 9.7918 | [13 empty] | 5 | 7.5 | bar: ODP 4 POLE to TEFC 6 POLE
|  | ODP or TEFC | ODP | With VFD | 1.0304 | 0.00641 | 1.0344 | 0.00996 | 1.0359 | 0.01121 | [6 empty] | 6 | 10
|  |  |  | DOL | 1.0781 | 0.03368 | 1.0713 | 0.02953 | 1.0716 | 0.03104 | [6 empty] | 7 | 15
|  | Number of Motor Poles | 4 | [13 empty] | 8 | 20
|  | Transmission | Direct | ODP 4 POLE: VFD Factors | [5 empty] | 9 | 25
|  | Quantity of VFD's | 1 | ODP 4 POLE: HP; ODP 6 POLE: d; ODP 8 POLE: e; TEFC 2 POLE: f | [5 empty] | 10 | 30
|  | Size of VFD's | 15 | Below | 15 | 0.98185 | 0.01985 | 0.0007 | [8 empty] | 11 | 40
|  |  |  | Above | 20 | 0.985 | 0.0175 | -0.0005 | [8 empty] | 12 | 50
|  |  |  | Linear interpol. | 0 | 0.98185 | 0.01985 | 0.0007 | [8 empty] | 13 | 60
[17 empty] | 14 | 75
[17 empty] | 15 | 100
BHP | Belt Efficiency ηb | Motor Shaft Power (HP) Hm | ηR | Lm | a | b | c | Motor Efficiency ηm | Lc | VFD effiiciency ηc | VFD & Motor Efficiency ηmc | Power Consumption kW | VFD, Motor & Transmission Efficiency ηsystem |  |  |  | 16 | 125
9.7918 | 1 | 9.7918 | 0.93 | 0.65279 | 1.0344 | 0.00996 | -0.024229 | 93.8% | 0.69596 | 95.51% | 89.59% | 8.1506 | 89.59% |  |  |  | 17 | 150
[17 empty] | 18 | 200
[17 empty] | 19 | 250
[17 empty] | 20 | 300 | bar: ODP 2 POLE
|  |  |  | ODP 2 POLE: ODP; TEFC 2 POLE: TEFC | [5 empty] | 21 | 350
|  |  | Fan System 2 | 2 POLE | 4 POLE | 6 POLE | 8 POLE | 2 POLE | 4 POLE | 6 POLE | 8 POLE | [5 empty] | 22 | 400
|  |  |  | 0.855 | 0.869 | 0.885 | 0.875 | 0.865 | 0.895 | 0.895 | 0.825 | [5 empty] | 23 | 450
|  | Quantity of Motors | 1 | [13 empty] | 24 | 500
|  | Motor Namplate Horsepower | 3 | ODP 2 POLE: Motor Factors; ODP 4 POLE: 2 POLE; ODP 8 POLE: 4 POLE; TEFC 4 POLE: 6 & 8 POLE | [5 empty] | 25
|  | Brake HP of 1 fan at design airflow | 2.4479 | [13 empty] | 26 | bar: ODP 4 POLE to TEFC 6 POLE
|  | ODP or TEFC | ODP | With VFD | 1.0327 | 0.01338 | 1.0402 | 0.02467 | 1.0676 | 0.0424 | [6 empty] | 37
|  |  |  | DOL | 1.1135 | 0.06436 | 1.1064 | 0.06571 | 1.1296 | 0.08027 | [6 empty] | 38
|  | Number of Motor Poles | 4 | [13 empty] | 39
|  | Transmission | Direct | ODP 4 POLE: VFD Factors | [5 empty] | 40
|  | Quantity of VFD's | 1 | ODP 4 POLE: HP; ODP 6 POLE: d; ODP 8 POLE: e; TEFC 2 POLE: f
|  | Size of VFD's | 3 | Below | 3 | 0.9789 | 0.0342 | -0.0079
|  |  |  | Above | 5 | 0.9775 | 0.0284 | -0.0027
|  |  |  | Linear interpol. | 0 | 0.9789 | 0.0342 | -0.0079
BHP | Belt Efficiency ηb | Motor Shaft Power (HP) Hm | ηR | Lm | a | b | c | Motor Efficiency ηm | Lc | VFD effiiciency ηc | VFD & Motor Efficiency ηmc | Power Consumption kW | VFD, Motor & Transmission Efficiency ηsystem
2.4479 | 1 | 2.4479 | 0.869 | 0.81598 | 1.0402 | 0.02467 | -0.015117 | 86.86% | 0.9394 | 93.71% | 81.4% | 2.2426 | 81.4%

## constantsHP
Table A1. EPCA Nominal Motor Efficiency (60 Hz motors) | [8 empty] | Table B1. Polyphase Induction Motor Performance Constants (hp rated motors with VFD) | [6 empty] | C1. VFD Performance Constants (hp capacity) | [5 empty] | Table D1. Polyphase Induction Motor Performance Constants (hp rated motors DOL)
| ODP |  |  |  | TEFC |  |  |  | HP | 2 POLE |  | 4 POLE |  | 6 & 8 POLE |  | HP | Index |  |  |  |  | HP | 2 POLE |  | 4 POLE |  | 6 & 8 POLE
| 2 POLE | 4 POLE | 6 POLE | 8 POLE | 2 POLE | 4 POLE | 6 POLE | 8 POLE |  | a | b | a | b | a | b |  |  | HP | d | e | f |  | a | b | a | b | a | b
1 | 77 | 83.5 | 82.5 | 75.5 | 77 | 85.5 | 82.5 | 72 | 1 | 1.0291 | 0.01701 | 1.0374 | 0.03337 | 1.0906 | 0.06457 | 1 | 0 | 1 | 0.9803 | 0.04 | -0.0131 | 1 | 1.1346 | 0.08674 | 1.1254 | 0.09132 | 1.1687 | 0.11466
1.5 | 84 | 86.5 | 86.5 | 77 | 84 | 86.5 | 87.5 | 75.5 | 1.5 | 1.03 | 0.0161 | 1.0381 | 0.0312 | 1.0848 | 0.05903 | 1.5 | 1 | 1.5 | 0.97995 | 0.03855 | -0.0118 | 1.5 | 1.1293 | 0.08114 | 1.1207 | 0.08492 | 1.1589 | 0.10606
2 | 85.5 | 86.5 | 87.5 | 86.5 | 85.5 | 86.5 | 88.5 | 81.5 | 2 | 1.0309 | 0.0152 | 1.0388 | 0.02902 | 1.0791 | 0.05349 | 2 | 1.5 | 2 | 0.9796 | 0.0371 | -0.0105 | 2 | 1.124 | 0.07555 | 1.1159 | 0.07851 | 1.1492 | 0.09747
3 | 85.5 | 86.9 | 88.5 | 87.5 | 86.5 | 89.5 | 89.5 | 82.5 | 3 | 1.0327 | 0.01338 | 1.0402 | 0.02467 | 1.0676 | 0.0424 | 3 | 2 | 3 | 0.9789 | 0.0342 | -0.0079 | 3 | 1.1135 | 0.06436 | 1.1064 | 0.06571 | 1.1296 | 0.08027
5 | 86.5 | 89.5 | 89.5 | 88.5 | 88.5 | 89.5 | 89.5 | 84 | 5 | 1.0364 | 0.00975 | 1.0429 | 0.01596 | 1.0446 | 0.02024 | 5 | 3 | 5 | 0.9775 | 0.0284 | -0.0027 | 5 | 1.0924 | 0.04197 | 1.0875 | 0.04009 | 1.0905 | 0.04588
7.5 | 88.5 | 91 | 90.2 | 89.5 | 89.5 | 91.7 | 91 | 84 | 7.5 | 1.0349 | 0.00892 | 1.0408 | 0.01446 | 1.0424 | 0.01798 | 7.5 | 5 | 7.5 | 0.9781 | 0.0253 | -0.0004 | 7.5 | 1.0888 | 0.0399 | 1.0834 | 0.03745 | 1.0858 | 0.04217
10 | 89.5 | 91.7 | 91.7 | 90.2 | 90.2 | 91.7 | 91 | 87.5 | 10 | 1.0334 | 0.00808 | 1.0387 | 0.01296 | 1.0402 | 0.01572 | 10 | 7.5 | 10 | 0.9787 | 0.0222 | 0.0019 | 10 | 1.0853 | 0.03783 | 1.0794 | 0.03481 | 1.0811 | 0.03846
15 | 90.2 | 93 | 91.7 | 90.2 | 91 | 92.4 | 91.7 | 87.5 | 15 | 1.0304 | 0.00641 | 1.0344 | 0.00996 | 1.0359 | 0.01121 | 15 | 10 | 15 | 0.98185 | 0.01985 | 0.0007 | 15 | 1.0781 | 0.03368 | 1.0713 | 0.02953 | 1.0716 | 0.03104
20 | 91 | 93 | 92.4 | 91 | 91 | 93 | 91.7 | 88.5 | 20 | 1.0273 | 0.00474 | 1.0302 | 0.00696 | 1.0315 | 0.0067 | 20 | 15 | 20 | 0.985 | 0.0175 | -0.0005 | 20 | 1.071 | 0.02953 | 1.0632 | 0.02425 | 1.0622 | 0.02362
25 | 91.7 | 93.6 | 93 | 91 | 91.7 | 93.6 | 93 | 88.5 | 25 | 1.0265 | 0.00476 | 1.0288 | 0.00642 | 1.0298 | 0.00622 | 25 | 20 | 25 | 0.9862 | 0.0165 | -0.0032 | 25 | 1.0695 | 0.02923 | 1.0603 | 0.02291 | 1.0597 | 0.02257
30 | 91.7 | 94.1 | 93.6 | 91.7 | 91.7 | 93.6 | 93 | 90.2 | 30 | 1.0257 | 0.00478 | 1.0274 | 0.00588 | 1.028 | 0.00575 | 30 | 25 | 30 | 0.9874 | 0.0155 | -0.0059 | 30 | 1.068 | 0.02892 | 1.0575 | 0.02157 | 1.0571 | 0.02152
40 | 92.4 | 94.1 | 94.1 | 91.7 | 92.4 | 94.1 | 94.1 | 90.2 | 40 | 1.0242 | 0.00481 | 1.0246 | 0.00479 | 1.0245 | 0.0048 | 40 | 30 | 40 | 0.98765 | 0.01695 | -0.0038 | 40 | 1.0651 | 0.02831 | 1.0518 | 0.01889 | 1.0521 | 0.01942
50 | 93 | 94.5 | 94.1 | 92.4 | 93 | 94.5 | 94.1 | 91 | 50 | 1.0226 | 0.00485 | 1.0218 | 0.0037 | 1.0211 | 0.00384 | 50 | 40 | 50 | 0.9879 | 0.0184 | -0.0017 | 50 | 1.0621 | 0.02769 | 1.0461 | 0.01621 | 1.047 | 0.01732
60 | 93.6 | 95 | 94.5 | 93 | 93.6 | 95 | 94.5 | 91 | 60 | 1.0223 | 0.00449 | 1.021 | 0.0035 | 1.0206 | 0.00399 | 60 | 50 | 60 | 0.9719 | 0.0145 | 0.0118 | 60 | 1.0595 | 0.02585 | 1.0444 | 0.01556 | 1.0455 | 0.01691
75 | 93.6 | 95 | 94.5 | 94.1 | 93.6 | 95.4 | 94.5 | 92.4 | 75 | 1.0217 | 0.00395 | 1.0197 | 0.0032 | 1.0198 | 0.0042 | 75 | 60 | 75 | 0.9919 | 0.0179 | -0.0013 | 75 | 1.0554 | 0.02309 | 1.0417 | 0.01459 | 1.0433 | 0.01631 | -0.02674
100 | 93.6 | 95.4 | 95 | 94.1 | 94.1 | 95.4 | 95 | 92.4 | 100 | 1.0209 | 0.00306 | 1.0176 | 0.00269 | 1.0186 | 0.00455 | 100 | 75 | 100 | 0.9824 | 0.0126 | 0.0014 | 100 | 1.0487 | 0.01849 | 1.0373 | 0.01298 | 1.0395 | 0.0153 | -0.024028
125 | 94.1 | 95.4 | 95 | 94.1 | 95 | 95.4 | 95 | 93 | 125 | 1.02 | 0.00299 | 1.0172 | 0.00286 | 1.0196 | 0.00459 | 125 | 100 | 125 | 0.98293 | 0.0119 | -0.0001 | 125 | 1.0471 | 0.01813 | 1.0373 | 0.01332 | 1.0395 | 0.01463
150 | 94.1 | 95.8 | 95.4 | 94.1 | 95 | 95.8 | 95.8 | 93 | 150 | 1.0191 | 0.00293 | 1.0169 | 0.00303 | 1.0205 | 0.00462 | 150 | 125 | 150 | 0.98345 | 0.0112 | -0.0016 | 150 | 1.0455 | 0.01778 | 1.0373 | 0.01365 | 1.0394 | 0.01396
200 | 95 | 95.8 | 95.4 | 94.1 | 95.4 | 96.2 | 95.8 | 93.6 | 200 | 1.0173 | 0.0028 | 1.0163 | 0.00336 | 1.0223 | 0.00468 | 200 | 150 | 200 | 0.9845 | 0.0098 | -0.0046 | 200 | 1.0423 | 0.01707 | 1.0373 | 0.01432 | 1.0393 | 0.01262
250 | 95 | 95.8 | 95.4 | 95 | 95.8 | 96.2 | 95.8 | 94.1 | 250 | 1.0173 | 0.0028 | 1.0163 | 0.00336 | 1.0223 | 0.00468 | 250 | 200 | 250 | 0.9845 | 0.0098 | -0.0046 | 250 | 1.0423 | 0.01707 | 1.0373 | 0.01432 | 1.0393 | 0.01262
300 | ODP 2 POLE: 95.4; ODP 4 POLE: 95.8; TEFC 2 POLE: 95.8; TEFC 4 POLE: 96.2 | 300 | 1.0173 | 0.0028 | 1.0163 | 0.00336 | 1.0223 | 0.00468 | 300 | 250 | 300 | 0.9845 | 0.0098 | -0.0046 | 300 | 1.0423 | 0.01707 | 1.0373 | 0.01432 | 1.0393 | 0.01262
350 | ODP 2 POLE: 95.4; ODP 4 POLE: 95.8; TEFC 2 POLE: 95.8; TEFC 4 POLE: 96.2 | 350 | 1.0173 | 0.0028 | 1.0163 | 0.00336 | 1.0223 | 0.00468 | 350 | 300 | 350 | 0.9845 | 0.0098 | -0.0046 | 350 | 1.0423 | 0.01707 | 1.0373 | 0.01432 | 1.0393 | 0.01262
400 | ODP 2 POLE: 95.8; ODP 4 POLE: 95.8; TEFC 2 POLE: 95.8; TEFC 4 POLE: 96.2 | 400 | 1.0173 | 0.0028 | 1.0163 | 0.00336 | 1.0223 | 0.00468 | 400 | 350 | 400 | 0.9845 | 0.0098 | -0.0046 | 400 | 1.0423 | 0.01707 | 1.0373 | 0.01432 | 1.0393 | 0.01262
450 | ODP 2 POLE: 95.8; ODP 4 POLE: 96.2; TEFC 2 POLE: 95.8; TEFC 4 POLE: 96.2 | 450 | 1.0173 | 0.0028 | 1.0163 | 0.00336 | 1.0223 | 0.00468 | 450 | 400 | 450 | 0.9845 | 0.0098 | -0.0046 | 450 | 1.0423 | 0.01707 | 1.0373 | 0.01432 | 1.0393 | 0.01262
500 | ODP 2 POLE: 95.8; ODP 4 POLE: 96.2; TEFC 2 POLE: 95.8; TEFC 4 POLE: 96.2 | 500 | 1.0173 | 0.0028 | 1.0163 | 0.00336 | 1.0223 | 0.00468 | 500 | 450 | 500 | 0.9845 | 0.0098 | -0.0046 | 500 | 1.0423 | 0.01707 | 1.0373 | 0.01432 | 1.0393 | 0.01262