Standards Report TC 10.1 & 10.3 

Chicago (January 21, 2018)
Submitted by:  Bruce Griffith
ASHRAE Standard 15:

· SSPC 15 met on Saturday (1/20) from 1 pm until 4 pm, Sunday (1/21) from 9 am until noon (working committee) and from 1 pm until 5 pm (main committee). 
· Summary of continuous maintenance:

· Addendum a – proposal to remove ammonia from Standard 15.  
· SPLS was presented with the proposed TPS (Title, Purpose, Scope) change.  They approved the removal of ammonia from the scope.  However, they did not approve the requirement within the scope to use IIAR 2.  The committee proposed an informative note to the scope which only references IIAR 2 for ammonia.
· There were 4 comments from the first public review.

· The addendum will go back out for public review on Feb. 2 and end March 4.
· Addendum d – new section 7.6 for class A2L refrigerants located in or directly serving occupied spaces (human comfort).  
· Addressed comments to the second public review and the committee is working through additional changes prior to sending out for a third public review.  
· Changes made to regulate both occupied and unoccupied spaces due to flammability (ex. Piping through spaces).
· Addendum h – class 2L refrigerants located in machinery rooms.  
· Addressed the first public review comments.  The committee will review modifications and letter ballot to send out for a second public review.

· Proposal to changed 8.11.6 for compliance with both subsections a and b.  Open flames using both combustion air from the machinery room and ensuring refrigerant detectors.  
· Proposal to modify section 5.3 – Changing Refrigerant and 7.5.1.7 - Mixing of Refrigerants.  The committee needs three letter ballots for approval to send to public review.

· The committee postponed the work on the re-write of the Standard until some of the addenda are released.  The main purpose of the re-write is to structure the standard in mandatory (code) language, eliminate redundancy and develop a logical format.  
· The subcommittee for 15.2, Safety Standard for Residential Refrigeration Systems, continues to work on a new standard.  A title, purpose and scope has been approved.  However, there were some recommendations for changes.  They will continue to meet monthly.
· Standard 15 & 34 – 2016 is available in the bookstore.

· A subcommittee was formed to review research conducted concerning connected spaces and the refrigerant concentration calculations.  They are still working on a proposal for updating the standard.
ASHRAE Standard 34:

· SSPC 34 meets Monday (1/22) evening 6:30 to 10 pm.  There are no new applications for refrigerants on the agenda.
· A public review for addendum G was sent out in the fall to make 2L a full class in lieu of a subclass.  There was a small error, so it will go out again for public review again this spring.  There will be a disconnect between 15 and 34, because 15 has not finalized 2L requirements.

Other Related Standards:
· UL 60335-2-40 – will stipulate A2 and A3 limits (heat pumps, hot water heaters, etc.).  A working group is addressing the use of A2 and A3 with charge limits up to 1kg.  Currently, the standard only permits A1 refrigerants.  The first public review received thousands of comments and the committee made several changes.  The second addition is now published for up to 15,000 volts.  Third addition (A2L) is out for public review until Feb.
· Brian Rodgers shared the UL 1995 transition to UL 60335-2-40 roadmap.  The UL 1995 standard will be discontinued in November 2020.    

Page 2 of 2

