NOTES from ASHRAE MEETING – NEW YORK

TRG4.IAQP

## January 19, 2014, 10:30 AM

## Sheraton Hotel, Conference Room K (Lower Level)

This was a small meeting: Chair Charlie Seyffer, Gemma Kerr, Chris Muller and Brian Hafendorfer.

Current issues

  - List of Contaminants of Concern: discussion continued as to whose list(s) should be used to generate the list for the Appendix of Standard 62.1. In Denver it was agreed to start with the 9 contaminants listed by WHO () (health-based list). The pilot IAQP credit from LEED is also health-based, quoting a list of 33 chemicals developed by California (some of these are really obscure, and this list is too long, we should aim for a short list, 8-12 chemicals). 62.1 cannot mention health, but this does not need to stop the Appendix using health as one of its criteria for making a list. ASHRAE Std. 189 is another potential source of useful info: they have a small list that includes formaldehyde, toluene, benzene and styrene.  Another decision that needs to be made is whether we simply list the chemicals or include a short write-up justifying inclusion.

  - Charlie is upset that the Handbook (Chapter 29) no longer supports using MERV 11-13 for particulate contaminant control. He wants this reinstated.

  - The aim at the NY meeting was to work on the office spaces write-up (see Charlie’s handout). This has several parts:

    - General intro, definition of spaces, likely contaminants, site survey, benefits of IAQP method, emphasize consultation, state minimum OA as 7.5 cfm/person (5 cfm/person is usually enough to supply the building exhausts and yield slight positive pressure, but we should use a safety factor);

    - Calculations for filter efficiency both particulate and gaseous per maths in body of standard.

    - Initial and (annual?) monitoring for commissioning and maintenance. Specify frequency, contaminants (same as design?, use 62.1 list, mostly NAAQS?, use list from BASE study?, add TVOC?). use third-party testing (Charlie says this is not always required)

    - Need to make sure potential users understand the differences between particulate and gaseous contaminant filters, ref efficiency and pressure drop change with use