## READ ME
When you choose the SELECT tab (below), you can:
Use the drop-down boxes: IP/SI and ROUND/RECT ®
Enter length and cross-section of duct ®
Take note of the size ranges permitted for acceptable data.
Graphs and tables will populate upon parameter entry.
Note: dotted lines on the curve are regression 2-sigmas.
You can print the page.
You can copy the page to paste into another file.
You can select just table items, for example to paste values
into a separate spreadsheet.
Check ASHRAE ON-LINE for Updates to this spreadsheet.
Note that attenuation values are capped at 50 dB, as flanking paths, etc. limit ultimate preformance.

## SELECT
Duct Liner Attenuation Calculator
based on RP-1408
Rev1 Apr 16, 2018
Click to ASHRAE ONLINE for updates
CHOOSE IP / SI => |  | IP
CHOOSE RECT / ROUND => |  | RECT
INPUT Length (ft) => |  | 15 | 3 <=L=< 26 ft |  | 15
INPUT Width ID (in) => |  | 36 | 12 <=W=< 48 in |  | 36
INPUT Height ID (in) => |  | 36 | 12 <=H=< 48 in |  | 36
| Perimeter | 144 |  | 144
| Area | 1296 |  | 1296
| P/A | 0.11111 |  | 0.11111
[8 empty] | RECTANGULAR DUCT | 36'' width ID x 36'' height ID, 15 ft long
[6 empty] | Freq. (Hz) | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
|  | Rectangular Duct 1/3-Octave Band Insertion Loss |  |  |  | 1'' liner | 0 | 1.2076 | 4.3533 | 15.9455 | 27.0927 | 12.5057 | 8.9295 | 7.5173
|  | 36'' width ID x 36'' height ID, 15 ft long |  |  |  | 2'' liner | 0.83821 | 3.5116 | 13.114 | 35.6965 | 20.5323 | 11.6442 | 9.5881 | 9.097
| Frequency (Hz) | 1'' Liner | 2'' Liner | Min | Max
| 50 | 0 | 1.6663 | -4.0601 | 7.3928
| 63 | 0 | 0.72265 | -5.8188 | 7.2641
| 80 | 0 | 0.24392 | -0.17116 | 0.65899
| 100 | 0.67664 | 2.1301 | -5.3972 | 6.7504
| 125 | 1.6682 | 3.9911 | 0.091463 | 5.5387
| 160 | 1.3374 | 4.8785 | 0.96694 | 6.7111
| 200 | 2.6881 | 9.8164 | 2.3935 | 12.6958
| 250 | 4.412 | 14.5093 | 4.0058 | 18.9236
| 315 | 6.9807 | 21.7162 | 5.8728 | 27.3624
| 400 | 12.0481 | 32.179 | 11.0231 | 35.3357
| 500 | 19.0481 | 40.7352 | 15.7473 | 45.812
| 630 | 28.3618 | 39.2741 | 25.6873 | 46.3709
| 800 | 32.0737 | 36.5129 | 26.983 | 46.0197
| 1000 | 28.7907 | 24.368 | 19.0243 | 33.233
| 1250 | 24.0695 | 16.4477 | 13.0897 | 29.6269
| 1600 | 16.1294 | 14.0803 | 8.855 | 20.1669
| 2000 | 12.61 | 11.5745 | 7.6544 | 15.5457
| 2500 | 10.4927 | 10.1424 | 6.8244 | 13.6736
| 3150 | 9.8344 | 9.8776 | 5.8648 | 13.8905
| 4000 | 8.9427 | 9.6914 | 5.456 | 13.9269
| 5000 | 8.1699 | 9.2217 | 3.9028 | 14.008
| 6300 | 7.8318 | 9.8608 | 1.5173 | 18.2043
| 8000 | 7.399 | 8.9107 | 2.7805 | 15.0409
| 10000 | 7.3375 | 8.6148 | 2.6035 | 14.6261

## Coeff+Calc (hidden)
[8 empty] | Raw Regression w/o Limits | Length | 15 |  | 0 | 0
[9 empty] | Width | 36 |  | 0
[7 empty] | 1296 |  | Height | 36 |  | 0
[9 empty] | P/A | 0.11111
Frequency | a1 | a2 | a3 | b1 | b2 | b3 |  | IL = (a1*P/A^2+a2*P/A+a3) + (b1*P/A^2+b2*P/A+b3) * L | [5 empty] | m-2s | s/m | m+2s
50 | -15.1074 | 24.6274 | -1.8048 | -10.9581 | 2.8118 | -0.17439 | 50 | 0.78627 | 50 | 0 |  | 63 | 0 | 0 | 2.1548 | 0
63 | 187.4808 | -61.4265 | 4.1482 | -38.2311 | 12.1593 | -0.81265 | 63 | 0.63358 | 63 | 0 |  | 125 | 1.2076 | 0 | 9.1354 | 0
80 | 53.4954 | -7.8505 | 0.17345 | 21.8759 | -6.4443 | 0.42039 | 80 | -0.42192 | 80 | 0 |  | 250 | 4.3533 | 0 | 1.6419 | 0
100 | -26.6911 | 9.0652 | -0.57076 | -7.9132 | 1.9162 | -0.077242 | 100 | 0.67664 | 100 | 0.67664 |  | 500 | 15.9455 | -5.3972 | 4.4882 | 6.7504
125 | 36.5266 | -16.752 | 1.4093 | -6.0275 | 3.2026 | -0.17014 | 125 | 1.6682 | 125 | 1.6682 |  | 1000 | 27.0927 | 0.091463 | 0.47259 | 3.245
160 | 66.4441 | -19.3704 | 1.2634 | 5.617 | -0.9065 | 0.12511 | 160 | 1.3374 | 160 | 1.3374 |  | 2000 | 12.5057 | 0.96694 | 0.13849 | 1.7078
200 | 31.2383 | -9.6 | 0.61541 | 2.4716 | 0.63537 | 0.082471 | 200 | 2.6881 | 200 | 2.6881 |  | 4000 | 8.9295 | 2.3935 | 0.054806 | 2.9828
250 | -0.55583 | 0.092305 | 0.14599 | -5.4624 | 3.7701 | -0.067297 | 250 | 4.412 | 250 | 4.412 |  | 8000 | 7.5173 | 4.0058 | 0.046025 | 4.8181
315 | 5.2697 | 0.73358 | 0.37521 | -0.24238 | 1.9398 | 0.21805 | 315 | 6.9807 | 315 | 6.9807 |  |  |  | 5.8728 | 0.079356 | 8.0886
400 | 49.6148 | -10.9043 | 1.93 | -9.7547 | 6.3464 | 0.12975 | 400 | 12.0481 | 400 | 12.0481 |  |  |  | 11.0231 | 0.042539 | 13.0732
500 | -35.3316 | 19.3463 | 0.85234 | -8.0895 | 7.3769 | 0.37904 | 500 | 19.0481 | 500 | 19.0481 |  |  |  | 15.7473 | 0.086646 | 22.349
630 | 315.0603 | -72.6004 | 6.4115 | -50.3438 | 21.8168 | -0.060737 | 630 | 28.3618 | 630 | 28.3618 |  |  |  | 25.6873 | 0.047149 | 31.0363
800 | 466.5094 | -140.8489 | 13.3884 | -103.7399 | 45.4594 | -1.8652 | 800 | 32.0737 | 800 | 32.0737 |  |  |  | 26.983 | 0.07936 | 37.1645
1000 | 138.9856 | -28.9129 | 7.2223 | -98.3774 | 55.8174 | -3.4497 | 1000 | 28.7907 | 1000 | 28.7907 |  |  |  | 24.3484 | 0.077148 | 33.233
1250 | 181.7617 | -28.1405 | 7.2381 | -33.7172 | 35.7091 | -2.3705 | 1250 | 24.0695 | 1250 | 24.0695 |  |  |  | 18.5121 | 0.11545 | 29.6269
1600 | -177.4592 | 92.4672 | -1.6983 | 102.2619 | -11.9166 | 0.7112 | 1600 | 16.1294 | 1600 | 16.1294 |  |  |  | 12.092 | 0.12516 | 20.1669
2000 | 46.4972 | 32.4742 | 0.96266 | 30.5321 | 0.51882 | 0.063087 | 2000 | 12.61 | 2000 | 12.61 |  |  |  | 9.6744 | 0.1164 | 15.5457
2500 | -141.8575 | 75.1282 | -1.472 | 36.5134 | -3.737 | 0.32233 | 2500 | 10.4927 | 2500 | 10.4927 |  |  |  | 7.3119 | 0.15157 | 13.6736
3150 | -0.6538 | 40.2695 | -0.22322 | 4.6775 | 3.5282 | -0.077015 | 3150 | 9.8344 | 3150 | 9.8344 |  |  |  | 7.4249 | 0.12251 | 12.244
4000 | 143.6422 | 1.7012 | 1.1549 | -14.7653 | 7.5841 | -0.27203 | 4000 | 8.9427 | 4000 | 8.9427 |  |  |  | 5.936 | 0.16811 | 11.9493
5000 | 146.5291 | -16.3802 | 2.7216 | -11.8526 | 7.9677 | -0.37502 | 5000 | 8.1699 | 5000 | 8.1699 |  |  |  | 3.9028 | 0.26115 | 12.437
6300 | 69.2372 | 9.5502 | 0.59426 | -11.8436 | 7.6202 | -0.34569 | 6300 | 7.8318 | 6300 | 7.8318 |  |  |  | 3.3301 | 0.2874 | 12.3336
8000 | 60.6108 | 15.6904 | 0.056944 | -16.4908 | 8.4168 | -0.40825 | 8000 | 7.399 | 8000 | 7.399 |  |  |  | 3.0608 | 0.29316 | 11.7373
10000 | 29.6992 | 29.2735 | -0.91913 | -17.6734 | 8.3423 | -0.39958 | 10000 | 7.3375 | 10000 | 7.3375 |  |  |  | 3.1166 | 0.28763 | 11.5584
Frequency | a1 | a2 | a3 | b1 | b2 | b3 |  | IL = (a1*P/A^2+a2*P/A+a3) + (b1*P/A^2+b2*P/A+b3) * L | [5 empty] | m-2s | s/m | m+2s
50 | -165.7464 | 74.4695 | -4.9626 | -17.2855 | 5.3367 | -0.35285 | 50 | 1.6663 | 50 | 1.6663 |  | 63 | 0.83821 | -4.0601 | 1.7183 | 7.3928
63 | 22.9099 | -7.5574 | 0.41543 | -12.5612 | 3.5848 | -0.18562 | 63 | 0.72265 | 63 | 0.72265 |  | 125 | 3.5116 | -5.8188 | 4.526 | 7.2641
80 | -102.512 | 36.0969 | -2.5783 | 30.5098 | -8.8163 | 0.60806 | 80 | 0.24392 | 80 | 0.24392 |  | 250 | 13.114 | -0.17116 | 0.85086 | 0.65899
100 | -30.1914 | 18.7959 | -1.536 | -15.5657 | 4.5515 | -0.18352 | 100 | 2.1301 | 100 | 2.1301 |  | 500 | 35.6965 | 0.1852 | 0.45653 | 4.0749
125 | 68.9423 | -22.9105 | 1.7947 | -2.954 | 3.2226 | -0.062207 | 125 | 3.9911 | 125 | 3.9911 |  | 1000 | 20.5323 | 2.4435 | 0.19388 | 5.5387
160 | 94.417 | -23.3026 | 1.5466 | 2.5204 | 1.0514 | 0.16909 | 160 | 4.8785 | 160 | 4.8785 |  | 2000 | 11.6442 | 3.0459 | 0.18783 | 6.7111
200 | 93.3175 | -31.3256 | 2.6214 | -6.989 | 5.7014 | 0.087697 | 200 | 9.8164 | 200 | 9.8164 |  | 4000 | 9.5881 | 6.937 | 0.14666 | 12.6958
250 | 67.358 | -27.6333 | 3.0311 | -14.187 | 9.6778 | 0.014301 | 250 | 14.5093 | 250 | 14.5093 |  | 8000 | 9.097 | 10.095 | 0.15212 | 18.9236
315 | 190.6176 | -65.2554 | 6.966 | -17.3667 | 11.0378 | 0.29782 | 315 | 21.7162 | 315 | 21.7162 |  |  |  | 16.0701 | 0.13 | 27.3624
400 | 25.2776 | -10.5432 | 3.0791 | -1.8622 | 8.4537 | 1.081 | 400 | 32.179 | 400 | 32.179 |  |  |  | 29.0222 | 0.049049 | 35.3357
500 | -218.5928 | 121.0682 | -6.0103 | -11.0525 | 6.3191 | 1.8338 | 500 | 40.7352 | 500 | 40.7352 |  |  |  | 35.6584 | 0.062314 | 45.812
630 | -339.8681 | 152.4021 | -4.0595 | -54.3503 | 34.5946 | -1.1331 | 630 | 39.2741 | 630 | 39.2741 |  |  |  | 32.1773 | 0.09035 | 46.3709
800 | 718.1961 | -225.0425 | 22.9718 | -261.6639 | 115.6004 | -7.6355 | 800 | 36.5129 | 800 | 36.5129 |  |  |  | 27.0062 | 0.13018 | 46.0197
1000 | 326.0399 | -69.2592 | 10.4327 | -19.6731 | 36.3456 | -2.6218 | 1000 | 24.368 | 1000 | 24.368 |  |  |  | 19.0243 | 0.10965 | 29.7118
1250 | -291.7838 | 104.0561 | -0.65204 | 159.2028 | -21.7874 | 1.0647 | 1250 | 16.4477 | 1250 | 16.4477 |  |  |  | 13.0897 | 0.10208 | 19.8057
1600 | -104.2919 | 52.6948 | 0.96326 | 43.7509 | -0.097183 | 0.040641 | 1600 | 14.0803 | 1600 | 14.0803 |  |  |  | 8.855 | 0.18555 | 19.3057
2000 | 57.3346 | 8.4349 | 2.7361 | 9.039 | 6.0365 | -0.30275 | 2000 | 11.5745 | 2000 | 11.5745 |  |  |  | 7.6544 | 0.16934 | 15.4945
2500 | 16.8446 | 9.4897 | 3.0033 | 7.4838 | 5.3135 | -0.29099 | 2500 | 10.1424 | 2500 | 10.1424 |  |  |  | 6.8244 | 0.16357 | 13.4604
3150 | 88.8154 | 0.89293 | 2.605 | -10.3765 | 8.9301 | -0.459 | 3150 | 9.8776 | 3150 | 9.8776 |  |  |  | 5.8648 | 0.20313 | 13.8905
4000 | 243.0797 | -37.0502 | 4.0657 | -30.8492 | 13.5721 | -0.67773 | 4000 | 9.6914 | 4000 | 9.6914 |  |  |  | 5.456 | 0.21852 | 13.9269
5000 | 162.5797 | -25.1019 | 4.0128 | -16.7875 | 10.3997 | -0.54887 | 5000 | 9.2217 | 5000 | 9.2217 |  |  |  | 4.4354 | 0.25951 | 14.008
6300 | 318.2925 | -79.5922 | 6.5725 | -41.5053 | 18.6038 | -1.0078 | 6300 | 9.8608 | 6300 | 9.8608 |  |  |  | 1.5173 | 0.42306 | 18.2043
8000 | 151.8582 | -18.6933 | 2.7974 | -30.4587 | 13.9523 | -0.75319 | 8000 | 8.9107 | 8000 | 8.9107 |  |  |  | 2.7805 | 0.34398 | 15.0409
10000 | 101.2175 | 4.2712 | 0.4563 | -28.236 | 12.3411 | -0.59369 | 10000 | 8.6148 | 10000 | 8.6148 |  |  |  | 2.6035 | 0.3489 | 14.6261
Freq | a1 | a2 | a3 | a4 | b1 | b2 | b3 | b4 | [8 empty] | m-2s | s/m | m+2s
50 | 0.00037657 | -0.029578 | 0.65788 | -3.1989 | -3.0679e-06 | 0.00049289 | -0.022756 | 0.31898 | 50 | -0.34828 | 50 | 0 |  | 63 | 0.44465 |  | 0 | 0.66135 | 0
63 | 0.00024702 | -0.028725 | 1.0237 | -9.9819 | 5.3097e-06 | -0.00028004 | 0.00036238 | 0.072234 | 63 | 0.71897 | 63 | 0.71897 |  | 125 | 1.1306 |  | -1.9335 | 1.8447 | 3.3715
80 | 3.8721e-05 | -0.0039744 | 0.11079 | -0.3566 | 1.1904e-05 | -0.0011156 | 0.031944 | -0.23527 | 80 | 0.65188 | 80 | 0.65188 |  | 250 | 3.8112 |  | -0.30602 | 0.73472 | 1.6098
100 | 0.00011389 | -0.01148 | 0.34162 | -2.5951 | -3.5544e-06 | 0.00048512 | -0.021443 | 0.34648 | 100 | 0.70002 | 100 | 0.70002 |  | 500 | 14.0303 |  | 0.21658 | 0.3453 | 1.1835
125 | -6.6156e-06 | 0.00078883 | -0.047109 | 0.98186 | -3.6337e-06 | 0.00054406 | -0.025938 | 0.4659 | 125 | 1.0149 | 125 | 1.0149 |  | 1000 | 21.1965 |  | 0.65825 | 0.1757 | 1.3715
160 | 7.3949e-05 | -0.0083348 | 0.28476 | -2.5359 | -1.2798e-05 | 0.001515 | -0.059223 | 0.85753 | 160 | 1.7416 | 160 | 1.7416 |  | 2000 | 10.4944 |  | 1.4275 | 0.090165 | 2.0557
200 | -1.1308e-05 | 0.00060834 | -0.0030781 | 0.24738 | -8.3495e-06 | 0.001158 | -0.054396 | 0.99444 | 200 | 2.609 | 200 | 2.609 |  | 4000 | 9.56 |  | 2.3358 | 0.052342 | 2.8821
250 | 8.0834e-05 | -0.0080682 | 0.227 | -1.5658 | -1.818e-05 | 0.0022369 | -0.092446 | 1.5174 | 250 | 3.5232 | 250 | 3.5232 |  | 8000 | 10.1292 |  | 3.2588 | 0.037519 | 3.7876
315 | 1.0011e-05 | -0.001981 | 0.087025 | -0.84137 | -2.2567e-05 | 0.0028729 | -0.12459 | 2.1979 | 315 | 5.94 | 315 | 5.94 |  |  |  |  | 5.6064 | 0.028086 | 6.2737
400 | -0.00017174 | 0.016345 | -0.49323 | 6.8307 | 3.0255e-06 | 0.00061082 | -0.066643 | 2.0082 | 400 | 10.3723 | 400 | 10.3723 |  |  |  |  | 9.0965 | 0.061501 | 11.6481
500 | 0.00010592 | -0.012394 | 0.39974 | -1.0806 | -2.3586e-06 | 0.0014156 | -0.1022 | 2.8732 | 500 | 15.9664 | 500 | 15.9664 |  |  |  |  | 13.7842 | 0.068338 | 18.1486
630 | 0.00045342 | -0.03928 | 0.93401 | 0.30074 | -3.7759e-05 | 0.0038903 | -0.14164 | 3.4228 | 630 | 28.2289 | 630 | 28.2289 |  |  |  |  | 23.368 | 0.086098 | 33.0897
800 | -0.00050209 | 0.051061 | -1.4787 | 19.8784 | 0.00011731 | -0.010596 | 0.21796 | 1.72 | 800 | 29.0162 | 800 | 29.0162 |  |  |  |  | 24.3771 | 0.07994 | 33.6553
1000 | 0.00037478 | -0.010934 | -0.77053 | 32.9906 | 9.693e-05 | -0.0098082 | 0.24617 | 0.27107 | 1000 | 22.7279 | 1000 | 22.7279 |  |  |  |  | 19.2143 | 0.077296 | 26.2414
1250 | -0.0011513 | 0.1435 | -5.8127 | 83.8104 | 0.00011749 | -0.011973 | 0.33732 | -1.3686 | 1250 | 17.9087 | 1250 | 17.9087 |  |  |  |  | 15.6894 | 0.061963 | 20.1281
1600 | -0.0014885 | 0.1748 | -6.6599 | 88.1356 | 8.2574e-05 | -0.0077791 | 0.18785 | -0.051519 | 1600 | 12.7063 | 1600 | 12.7063 |  |  |  |  | 11.1693 | 0.060484 | 14.2434
2000 | -0.00078111 | 0.10074 | -4.3068 | 65.2322 | 7.9478e-06 | -0.00022883 | -0.033177 | 1.4997 | 2000 | 9.9997 | 2000 | 9.9997 |  |  |  |  | 8.4672 | 0.076626 | 11.5322
2500 | -0.00031902 | 0.042601 | -1.923 | 35.1344 | -5.1727e-05 | 0.0061917 | -0.25087 | 3.6334 | 2500 | 9.4277 | 2500 | 9.4277 |  |  |  |  | 8.0572 | 0.072681 | 10.7981
3150 | 0.00064689 | -0.052982 | 1.0478 | 5.5312 | -8.419e-05 | 0.0091305 | -0.33247 | 4.3713 | 3150 | 9.3822 | 3150 | 9.3822 |  |  |  |  | 8.1171 | 0.067419 | 10.6473
4000 | 0.0010572 | -0.098761 | 2.6045 | -9.0974 | -8.712e-05 | 0.0092754 | -0.32188 | 3.8356 | 4000 | 9.0624 | 4000 | 9.0624 |  |  |  |  | 7.5924 | 0.081104 | 10.5324
5000 | 0.0007877 | -0.076488 | 2.0286 | -3.2592 | -4.2905e-05 | 0.0046461 | -0.16472 | 2.1063 | 5000 | 10.3338 | 5000 | 10.3338 |  |  |  |  | 8.0573 | 0.11015 | 12.6104
6300 | 0.00085407 | -0.08158 | 2.0814 | -2.1448 | -3.0885e-05 | 0.0034961 | -0.12949 | 1.78 | 6300 | 10.0297 | 6300 | 10.0297 |  |  |  |  | 7.8278 | 0.10977 | 12.2316
8000 | 0.0010456 | -0.10062 | 2.6429 | -6.7438 | -3.6658e-05 | 0.0039189 | -0.13472 | 1.7139 | 8000 | 10.2705 | 8000 | 10.2705 |  |  |  |  | 8.1001 | 0.10566 | 12.441
10000 | 0.0017282 | -0.17306 | 5.0364 | -31.0765 | -0.00010878 | 0.011418 | -0.3767 | 4.0724 | 10000 | 10.0911 | 10000 | 10.0911 |  |  |  |  | 5.0141 | 0.25156 | 15.168
Freq | a1 | a2 | a3 | a4 | b1 | b2 | b3 | b4 | [8 empty] | m-2s | s/m | m+2s
50 | 0.00013071 | -0.0057135 | -0.087046 | 4.6762 | -6.1409e-06 | 0.00072483 | -0.025317 | 0.28366 | 50 | 0.61273 | 50 | 0.61273 |  | 63 | 1.1219 |  | -0.010568 | 0.50862 | 1.236
63 | 0.00036032 | -0.036376 | 1.0926 | -8.3126 | -1.2919e-05 | 0.0013717 | -0.045656 | 0.51111 | 63 | 1.3261 | 63 | 1.3261 |  | 125 | 3.4792 |  | -0.45021 | 0.66975 | 3.1025
80 | 7.1001e-05 | -0.0027481 | -0.077676 | 2.7651 | -9.051e-06 | 0.00092264 | -0.033456 | 0.54809 | 80 | 1.4768 | 80 | 1.4768 |  | 250 | 10.1267 |  | 0.64201 | 0.28264 | 2.3117
100 | 0.00010795 | -0.0087173 | 0.1847 | -0.33164 | -1.7713e-05 | 0.0019349 | -0.071425 | 1.0551 | 100 | 2.5313 | 100 | 2.5313 |  | 500 | 33.382 |  | 1.6814 | 0.16788 | 3.3812
125 | 2.4065e-05 | 0.0013932 | -0.20341 | 4.1277 | -1.2709e-05 | 0.0014973 | -0.062295 | 1.1266 | 125 | 3.2066 | 125 | 3.2066 |  | 1000 | 21.4427 |  | 2.4865 | 0.11229 | 3.9267
160 | 4.0456e-05 | -0.0013819 | -0.049374 | 1.6145 | -1.9744e-05 | 0.0023113 | -0.096886 | 1.7569 | 160 | 5.0826 | 160 | 5.0826 |  | 2000 | 10.8764 |  | 4.5322 | 0.05415 | 5.6331
200 | -7.23e-05 | 0.0085794 | -0.3215 | 3.9515 | -1.8895e-05 | 0.0025345 | -0.11948 | 2.3723 | 200 | 7.2351 | 200 | 7.2351 |  | 4000 | 10.9653 |  | 6.8713 | 0.02514 | 7.5989
250 | 2.0118e-05 | -0.00074435 | -0.039827 | 1.6892 | -3.2133e-05 | 0.0042397 | -0.18693 | 3.4133 | 250 | 10.419 | 250 | 10.419 |  | 8000 | 10.2594 |  | 9.7189 | 0.033596 | 11.119
315 | 0.00014155 | -0.011146 | 0.24691 | -1.037 | -7.4859e-05 | 0.0083854 | -0.31295 | 5.182 | 315 | 19.3704 | 315 | 19.3704 |  |  |  |  | 18.5973 | 0.019954 | 20.1435
400 | 0.00065536 | -0.056012 | 1.3376 | 2.1205 | -3.5525e-05 | 0.0038618 | -0.14445 | 3.3262 | 400 | 30.3597 | 400 | 30.3597 |  |  |  |  | 24.3975 | 0.098193 | 36.3219
500 | 0.00062247 | -0.052521 | 1.2376 | 8.6697 | -1.6623e-05 | 0.0021047 | -0.091814 | 2.6697 | 500 | 33.9465 | 500 | 33.9465 |  |  |  |  | 24.4377 | 0.14005 | 43.4552
630 | -0.00057779 | 0.027702 | -0.08863 | 15.8836 | -0.00012486 | 0.01363 | -0.49416 | 7.3561 | 630 | 42.7255 | 630 | 42.7255 |  |  |  |  | 32.8469 | 0.11561 | 52.6041
800 | 0.0012738 | -0.10575 | 1.9176 | 22.0286 | 4.6142e-05 | -0.006037 | 0.20452 | -0.41728 | 800 | 32.5448 | 800 | 32.5448 |  |  |  |  | 26.5187 | 0.092581 | 38.5708
1000 | -0.0010981 | 0.13752 | -5.6623 | 86.0461 | 0.00027332 | -0.027693 | 0.81487 | -5.23 | 1000 | 23.704 | 1000 | 23.704 |  |  |  |  | 19.2514 | 0.09392 | 28.1565
1250 | -0.0026454 | 0.28901 | -10.3026 | 127.1209 | 0.00017443 | -0.017474 | 0.50643 | -3.0299 | 1250 | 17.7724 | 1250 | 17.7724 |  |  |  |  | 15.3845 | 0.06718 | 20.1603
1600 | -0.0017763 | 0.19149 | -6.7962 | 86.2552 | 3.2867e-05 | -0.0019445 | -0.024481 | 2.2611 | 1600 | 12.7862 | 1600 | 12.7862 |  |  |  |  | 10.842 | 0.076028 | 14.7304
2000 | -0.00024768 | 0.020926 | -0.79181 | 19.7662 | -0.00017035 | 0.020271 | -0.78472 | 10.1477 | 2000 | 10.1331 | 2000 | 10.1331 |  |  |  |  | 6.8755 | 0.16074 | 13.3908
2500 | -0.00085723 | 0.085996 | -2.9397 | 41.9624 | -4.067e-05 | 0.0056398 | -0.2506 | 3.7839 | 2500 | 10.1976 | 2500 | 10.1976 |  |  |  |  | 7.6345 | 0.12567 | 12.7607
3150 | -1.0587e-06 | -0.002223 | -0.12309 | 14.2282 | -6.3133e-05 | 0.0078072 | -0.31535 | 4.4381 | 3150 | 10.7369 | 3150 | 10.7369 |  |  |  |  | 8.6997 | 0.094871 | 12.7742
4000 | 0.00032092 | -0.040945 | 1.2494 | 1.8259 | -5.8647e-05 | 0.0072745 | -0.28474 | 3.6994 | 4000 | 10.8195 | 4000 | 10.8195 |  |  |  |  | 7.8663 | 0.13647 | 13.7727
5000 | 0.00048782 | -0.058099 | 1.7538 | -1.5503 | -2.3816e-05 | 0.0034935 | -0.14993 | 2.1356 | 5000 | 11.3661 | 5000 | 11.3661 |  |  |  |  | 8.4173 | 0.12972 | 14.3149
6300 | 0.00067743 | -0.071866 | 1.9389 | -0.12667 | -1.2177e-05 | 0.0022206 | -0.10406 | 1.6047 | 6300 | 10.6649 | 6300 | 10.6649 |  |  |  |  | 8.2128 | 0.11496 | 13.1171
8000 | 0.001029 | -0.10187 | 2.6621 | -4.6723 | -2.3177e-05 | 0.0029678 | -0.11216 | 1.4809 | 8000 | 10.2754 | 8000 | 10.2754 |  |  |  |  | 8.2531 | 0.098407 | 12.2978
10000 | 0.0016914 | -0.16215 | 4.3144 | -18.1559 | -5.4465e-05 | 0.0054387 | -0.15975 | 1.507 | 10000 | 9.8739 | 10000 | 9.8739 |  |  |  |  | 7.7537 | 0.10736 | 11.9941